## Component_Library
Component_ID | Component_Name | Vendor_Part_No | Category | Subcategory | Pump_Model_Compatibility | Vendor_Name | Qty_Per_Unit | Unit | Material_Spec | Weight_kg | Lead_Time_Days | Notes
PUMP-FLW-LNN600 | Pump Assembly - Flowserve 300-LNN-600 | MS2425801 | Pump | Centrifugal Horizontal | Flowserve 300-LNN-600 | Flowserve | 1 | EA | Various (See Components) | 1160 |  | Double suction horizontally split case, Single stage
CAS-FLW-001 | Volute Casing 300-LNN-600 |  | Casing | Pump Hydraulics | Flowserve 300-LNN-600 | Flowserve | 1 | EA | ASTM A216 WCB |  |  | Horizontally split, PN16 rating
IMP-FLW-001 | Impeller Closed Type |  | Impeller | Pump Hydraulics | Flowserve 300-LNN-600 | Flowserve | 1 | EA | 12% Chrome Steel A487 |  |  | Diameter: 600mm rated, 480mm min, 600mm max
SHAFT-FLW-001 | Pump Shaft |  | Shaft | Rotating | Flowserve 300-LNN-600 | Flowserve | 1 | EA | EN-19 / SS410
WRNG-FLW-001 | Casing Wear Ring |  | Wear Ring | Pump Hydraulics | Flowserve 300-LNN-600 | Flowserve | 1 | EA | ASTM A487 Gr CA6M CI.B
SHAFT-SLV-001 | Shaft Sleeve |  | Sleeve | Rotating | Flowserve 300-LNN-600 | Flowserve | 1 | EA | ASTM A216 Type 420
BRG-FLW-001 | Bearing DE | 6217 C3 | Bearing | Radial Ball | Flowserve 300-LNN-600 | SKF/FAG | 1 | EA | Steel |  |  | Oil lubricated ISO VG 32
BRG-FLW-002 | Bearing NDE | 7217 | Bearing | Radial Ball | Flowserve 300-LNN-600 | SKF/FAG | 1 | EA | Steel |  |  | Oil lubricated ISO VG 32
BRG-HSG-001 | Bearing Housing |  | Housing | Bearing Support | Flowserve 300-LNN-600 | Flowserve | 1 | EA | ASTM A48 CI.30
SEAL-FLW-001 | Mechanical Seal Single Cartridge |  | Seal | Mechanical Seal | Flowserve 300-LNN-600 | Flowserve Sanmar | 1 | EA | As per seal drawing |  |  | Plan 11, 62
MOT-CGL-550 | Motor 550kW 4-Pole VFD | 2241805 | Motor | Induction Motor | Flowserve 300-LNN-600 | CGL (Crompton Greaves) | 1 | EA | Cast Iron Frame | 5300 |  | Frame NG450, 690V, 50Hz, IC411, VFD driven 1143-1233 rpm
CPLG-RTH-001 | Coupling Spacer Tyre Type |  | Coupling | Flexible Coupling | Flowserve 300-LNN-600 | Rathi | 1 | EA | Steel/Rubber | 50 |  | DBSE 250mm, GD² = 11.6 kg·m²
BASE-FLW-001 | Baseplate Fabricated |  | Baseplate | Structural | Flowserve 300-LNN-600 | Flowserve | 1 | EA | IS 2062 | 3250 |  | Drain pan type, grouted
ENCL-FLW-001 | Acoustic Enclosure |  | Enclosure | Acoustic | Flowserve 300-LNN-600 | ARK (Acoustic) | 1 | EA | Modular Panels | 2350 |  | Noise reduction to <85 dBA
BOLT-FDN-001 | Foundation Bolt M20 |  | Fastener | Foundation Bolt | Flowserve 300-LNN-600 | Local | 14 | EA | ASTM A193 Gr.B7 |  |  | With nuts A194 2H
THERM-001 | Dial Type Thermometer |  | Instrumentation | Temperature | Flowserve 300-LNN-600 | Local | 2 | EA | SS316 |  |  | Bearing temperature monitoring
PUMP-KSB-V5036 | Pump Assembly - KSB RPH-V 50-360 | 9975830001-500/700/900 | Pump | Centrifugal Vertical | KSB RPH-V 50-360 | KSB | 1 | EA | Various (See Components) | 410 |  | Vertical submersible, API 610 12th Ed., 3 units for IOCL
CAS-KSB-001 | Volute Casing RPH-V 50-360 CL300 | 5557702 | Casing | Pump Hydraulics | KSB RPH-V 50-360 | Jsons Foundry | 1 | EA | Cast Iron/CS UG2477594 |  | 21 | Main casing for vertical pump
IMP-KSB-001 | Impeller RPH-V 50-360 | 5557704 | Impeller | Pump Hydraulics | KSB RPH-V 50-360 | Jsons Foundry | 1 | EA | CF8M (SS316) Z05236300 |  | 21 | Hydraulic impeller
CAS-CVR-001 | Casing Cover RPH-V 50-360 | 5557703 | Casing | Cover | KSB RPH-V 50-360 | Stock | 1 | EA | CL300 RF Z0 |  | 0 | Casing cover
BRG-HSG-KSB | Bearing Housing RPH-V | 5551361 | Housing | Bearing Support | KSB RPH-V 50-360 | Jsons Foundry | 1 | EA | Cast |  | 105 | Bearing housing
BRG-CVR-KSB | Bearing Cover RPH-V | 5557705 | Cover | Bearing | KSB RPH-V 50-360 | Stock | 1 | EA | UG15278600000 |  | 0
OIL-KSB-001 | Constant Level Oiler NPT1/4 | IN010767 | Lubrication | Oiler | KSB RPH-V 50-360 | Stock | 1 | EA | Steel/Glass |  | 0
BRK-KSB-001 | Bearing Bracket LANT RPH-V | 5276186 | Bracket | Support | KSB RPH-V 50-360 | Swaraj Engineering | 1 | EA | MS |  | 28
ROD-KSB-001 | Rod 65DIA | 5454414 | Shaft | Rod | KSB RPH-V 50-360 | Stock | 1 | EA | Steel |  | 0
MOT-LXM-45 | Motor 45kW Frame 225M | 5548523 | Motor | Induction Motor | KSB RPH-V 50-360 | Laxmi Hydraulics | 1 | EA | Cast Iron | ~750 | 0 | IE3 TEFC, 3 units required
MOT-PRT-001 | Motor Parts for 9975830001-500 | 5560014 | Motor | Accessories | KSB RPH-V 50-360 | Laxmi Hydraulics | 1 | LOT | Various |  | 0 | Motor accessories
CPLG-KSB-001 | Coupling for 9975830001-500/700/900 | 5550100 | Coupling | Flexible | KSB RPH-V 50-360 | Unique Transmission | 1 | EA | Steel |  | 45 | Standard coupling, 3 units
SEAL-JC-001 | Mechanical Seal JC-48SC Single Cartridge | 5552319 | Seal | Mechanical Seal | KSB RPH-V 50-360 | John Crane | 1 | EA | SiC/SiC/Viton |  | 38 | Single cartridge seal, 9 units total
BASE-KSB-001 | Soleplate RPH-V 50-360 CIRC | 5576296 | Baseplate | Mounting | KSB RPH-V 50-360 | J.J. Engineers | 1 | EA | Fabricated MS |  | 50 | Mounting plate, 3 units
GUARD-KSB-001 | Coupling Guard 320X450 BWG15 | 5541895 | Guard | Safety | KSB RPH-V 50-360 | Sai Technofab | 1 | EA | SS304/MS |  | 30 | Safety guard, 3 units
PIPE-SUSP-001 | Delivery Suspension Pipe DN100-1100 | 5571613-14-15 | Piping | Column | KSB RPH-V 50-360 | Swaraj Engineering | 1 | EA | CS |  | 21 | 9 units - delivery suspension
PIPE-COL-001 | Column Pipe DN40-80-CIR-2473X6 | 5571618 | Piping | Column | KSB RPH-V 50-360 | Swaraj Engineering | 1 | EA | CS |  | 28 | 9 units - column pipe
STR-DN50-001 | Strainer DN50X160X220 CL300 | 5508101 | Strainer | Suction | KSB RPH-V 50-360 | Jay-Eesh Engineering | 1 | EA | CS |  | 35
STOOL-KSB-001 | Motor Stool RPH-V FR 225M | 05582384 | Stool | Support | KSB RPH-V 50-360 | Swaraj Engineering | 1 | EA | Fabricated MS | ~56 | 38 | 3 units - motor support
PUMP-KSB-V4018 | Pump Assembly - KSB RPH-V 40-180 | 9975830001-1100 | Pump | Centrifugal Vertical | KSB RPH-V 40-180 | KSB | 1 | EA | Various | ~350 |  | Vertical submersible, 1 unit for IOCL
CAS-KSB-002 | Volute Casing RPH-V 40-180 CL300 | 5550408 | Casing | Pump Hydraulics | KSB RPH-V 40-180 | Stock | 1 | EA | UG1700 |  | 0
IMP-KSB-002 | Impeller RPH 40-180 | 5550412 | Impeller | Pump Hydraulics | KSB RPH-V 40-180 | KSB Pumps Foundries | 1 | EA | Z052379 |  | 21
CAS-CVR-002 | Casing Cover RPH-V 40-180 | 5550414 | Casing | Cover | KSB RPH-V 40-180 | Stock | 1 | EA | Z042521-01 |  | 0
MOT-LXM-5.5 | Motor 5.5kW Frame 132S | 05548522 | Motor | Induction Motor | KSB RPH-V 40-180 | Laxmi Hydraulics | 1 | EA | Cast Iron | ~250 | 0 | IE3 TEFC, 1 unit
CPLG-KSB-002 | Coupling for 9975830001-1100 | 05550089 | Coupling | Flexible | KSB RPH-V 40-180 | Unique Transmission | 1 | EA | Steel |  | 45 | Smaller coupling
BASE-KSB-002 | Soleplate RPHV40-181/B D24IN | 05550421 | Baseplate | Mounting | KSB RPH-V 40-180 | The Sky Industries | 1 | EA | Fabricated MS |  | 50
STOOL-KSB-002 | Motor Stool RPH-V FR 132 S/M2P/4P | 5479064 | Stool | Support | KSB RPH-V 40-180 | Stock | 1 | EA | Fabricated MS |  | 0
PUMP-METSO-HM200 | Pump Assembly - Metso HM200 MHC-S C5 DDE | SAL537200 | Pump | Centrifugal Horizontal Slurry | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | Various | 944.7 |  | HM200 bare pump; single stage; V-belt driven; impeller dia 500mm; suction NPS8" ANSI300; discharge NPS6" ANSI300
CAS-METSO-001 | Casing Module HM200 C5/W9 (GPS800) | SAL532662-W1 | Casing | Pump Hydraulics | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | ASTM A532 GR.IIIA (GPS800) | 375.1 |  | Single volute casing; includes Case HM200 (PDCH2034, 321.2kg) + Back Liner (PDCH2021, 53.9kg); hydro test 16 bar g
CAS-METSO-002 | Case HM200 GPS800 | PDCH2034 | Casing | Pump Hydraulics | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | ASTM A532 GR.IIIA (GPS800) | 321.2 |  | Main volute casing body; ANSI 300 flanges
CAS-METSO-003 | Back Liner FR500 GPS800 | PDCH2021 | Casing | Pump Hydraulics | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | ASTM A532 GR.IIIA (GPS800) | 53.9 |  | Back liner; wear part
IMP-METSO-001 | Pump Impeller HM200 C5 GPS800 (Machined) | PDCH2019 | Impeller | Pump Hydraulics | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | ASTM A532 GR.IIIA (GPS800) | 130.2 |  | Closed type; fixed diameter 500mm; 5-vane; max sphere 65mm; GD2=5.08 kgm²
IMP-METSO-002 | Billet Pump Impeller HM200 C5 GPS800 (Raw) | PDCH2019-01 | Impeller | Pump Hydraulics | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | ASTM A532 GR.IIIA (GPS800) | 130.7 |  | Pre-machined billet impeller; spare/commissioning
BRG-METSO-001 | Bearing Assembly FR500-S DDE | PDWB062-S | Bearing | Bearing Frame | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | Steel | 145.9 |  | Double drive end (DDE) taper roller bearing assembly; TIMKEN make; grease lubricated
BRG-METSO-002 | Bearing Frame FR500-S | 500648-M2 | Bearing | Bearing Frame | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | IS:2062 MS | 199.9 |  | Bearing frame housing structure
FRM-METSO-001 | Frame Assembly (Frame Module FR500) | SAL534463-P1 | Frame | Structural | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | MS TZN coated | 205.4 |  | Complete frame module; includes saddle, fasteners; bearing frame 199.9kg
SEAL-METSO-001 | Mechanical Seal Single FR500 with Adaptor | AX03-900016694 | Seal | Shaft Sealing | Metso HM200 MHC-S C5 DDE | Flowserve SANMAR Ltd | 1 | EA | Various (316SS, ceramic, etc.) | 34.9 |  | Flowserve model 2H-104764; single mech seal with SLD (Synthetic Lubricating Device); API Plan 62; cartridge type; 5.875" size
SEAL-METSO-002 | Shaft Sleeve FR500 | PDCH5050 | Seal | Shaft Sealing | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | SS316 (1.4436) | 4.4 |  | Shaft sleeve under seal; CH5050 dwg
SEAL-METSO-003 | Gland Guard Kit FR500 | SAL530154-M1 | Seal | Shaft Sealing | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | Steel | 1.4 |  | Gland guard (upper SAL529575-M1 + lower 501454-1)
FLG-METSO-001 | Flange Assembly NPS 8" ANSI 300LB (Suction) | 504079-M1 | Flange | Nozzle | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | Carbon Steel 1.0045 | 27.3 |  | Suction flange; 2x half flanges (12.8kg each) + bolts/nuts; ANSI/ASME B16.5 Class 300
FLG-METSO-002 | Flange Assembly NPS 6" ANSI 300LB (Discharge) | 500680-M1 | Flange | Nozzle | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | Carbon Steel 1.0045 | 11.4 |  | Discharge flange; 2x half flanges (5.6kg each); ANSI/ASME B16.5 Class 300
GSK-METSO-001 | Gasket Inlet/Outlet (Suction side) | PD731032 | Gasket | Sealing | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | NR 70° SH (NBR) | 0.1 |  | CH2478 spec; NPS8" inlet gasket
GSK-METSO-002 | Gasket Inlet/Outlet (Discharge side) | PD701032 | Gasket | Sealing | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | NR 70° SH (NBR) | 0.1 |  | CH2478 spec; NPS6" outlet gasket
GSK-METSO-003 | O-Ring SMS1586-99.50X3.00-NBR70 | SA953201 | Gasket | Sealing | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 2 | EA | NBR 70 Shore | 0 |  | 2 off per pump; casing sealing
GSK-METSO-004 | O-Ring 350x5 NBR (Casing) | SA959120 | Gasket | Sealing | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | NBR | 0 |  | Case module O-ring seal
SHM-METSO-001 | Case Shim Module FR500-S PVC | SAL535831-P1 | Shim | Alignment | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | PVC-U | 0.2 |  | 2mm shims; max 2 per side for impeller clearance adjustment
FST-METSO-001 | Wet End Fasteners Assembly HM200/MM250-S | SAL535225-W1 | Fasteners | Structural | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | SET | Steel TZN coated | 8.3 |  | Includes T-bolts M16x90, case bolt kit M24x110, nuts, washers; 16B C/W TZN
SDL-METSO-001 | Saddle FR500 | 500729-1 | Saddle | Structural | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | JL1030 Cast Iron | 1.8 |  | Pump casing support saddle
SGN-METSO-001 | Sign Kit Right Rotating Pump FR250 | 500125-S1-IN | Nameplate | Accessories | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA |  | 0 |  | Rotation direction sign kit
VBL-METSO-001 | V-Belt Set 10 x 8V-1600 (4060mm length) |  | V-Belt | Power Transmission | Metso HM200 MHC-S C5 DDE | Fenner | 10 | EA | Rubber/Fabric |  |  | 8V section; 10 belts per pump; motor to pump drive
VBL-METSO-002 | Motor Pulley 500 PCD, 10 Groove 8V |  | Pulley | Power Transmission | Metso HM200 MHC-S C5 DDE | Fenner | 1 | EA | Steel |  |  | Motor side pulley; 500mm PCD; Bush 5050/D110
VBL-METSO-003 | Pump Pulley 500 PCD, 10 Groove 8V |  | Pulley | Power Transmission | Metso HM200 MHC-S C5 DDE | Fenner | 1 | EA | Steel |  |  | Pump side pulley; 500mm PCD; Bush 5050/D80
MOT-METSO-001 | Motor Innomotics HV 500kW 4-Pole 690V VFD (1LA4400-4AW00-Z) | 3000021569/000100 | Motor | Electrical Drive | Metso HM200 MHC-S C5 DDE | Innomotics India Pvt Ltd (formerly Siemens Large Drives) | 1 | EA | Cast Iron Frame | 3400 |  | IEC400 frame; 500kW; 690V; 4-pole; 1491rpm; IP55; IC411; VFD suitable (SINAMICS GH180); S1 duty; Therm.class 155F/130B; 3ph 50Hz; IN=570A
MOT-METSO-002 | Motor DE Bearing SKF NU328E | NU328E | Bearing | Motor Components | Metso HM200 MHC-S C5 DDE | SKF | 1 | EA | Steel |  |  | Motor drive end bearing; DIN5412; grease lube; ESSO UNIREX N3; 2000hr regreasing
MOT-METSO-003 | Motor NDE Bearing SKF 6224C3 Insulated | 6224C3 | Bearing | Motor Components | Metso HM200 MHC-S C5 DDE | SKF | 1 | EA | Steel (electrically insulated) |  |  | Motor non-drive end bearing; DIN625; electrically insulated; grease lube; ESSO UNIREX N3
BPL-METSO-001 | Bed Frame with Motor Support |  | Baseplate | Structural | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | MS / Structural Steel | 792 |  | Common base frame for pump and motor; grouted; M24 anchor bolts; paint RAL7033
GRD-METSO-001 | V-Belt Guard |  | Guard | Safety | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | EA | Steel | 107 |  | Belt drive guard; covers motor-to-pump belt drive
ASM-METSO-001 | Complete Pump Set Assembly (Pump+Motor+Frame+Guard) | ZT2023.02-508-VEN-MEC-002 | Assembly | Complete Set | Metso HM200 MHC-S C5 DDE | Metso Outotec India Pvt Ltd | 1 | SET | Various | 5390 |  | Total assembly weight from GA drawing SAL537200; pump 1010kg + motor 3400kg + frame 792kg + guard 107kg
CAS-FLW-001 | Pump Casing Upper Half 300-LNN-600 | MS2425801-CAS-U | Casing | Upper Casing | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | EA | Carbon Steel (CS) | 272 | 90 | Top half; weight 272 kg from GA. Test pressure 24 barg. Horizontal split casing. Suction 350mm / Discharge 300mm. PN16 FF flanges
CAS-FLW-002 | Pump Casing Lower Half 300-LNN-600 | MS2425801-CAS-L | Casing | Lower Casing | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | EA | Carbon Steel (CS) |  | 90 | Lower half. Total pump wt 1160 kg incl rotor 173 kg + top casing 272 kg. Lower casing ~715 kg (calculated: 1160-272-173)
IMP-FLW-001 | Impeller 300-LNN-600 (Trimmed) | MS2425801-IMP | Impeller | Closed Impeller | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | EA | Carbon Steel (CS) |  | 90 | Impeller trimmed per actual performance. Q=961 m3/h, H=86m. Part of rotor assembly (rotor total 173 kg). Material: Carbon Steel per nameplate
RTR-FLW-001 | Pump Rotor Assembly 300-LNN-600 | MS2425801-RTR | Rotor | Rotor Assembly | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | EA | Carbon Steel (CS) | 173 | 90 | Complete rotor assembly weight 173 kg from GA drawing. Includes impeller + shaft + keys + wear rings
SEAL-FLW-001 | Mechanical Seal 300-LNN-600 | MS2425801-SEAL | Mechanical Seal | Cartridge Seal | Flowserve 300-LNN-600 | Flowserve Sanmar | 2 | EA | MOC per Flowserve seal drawing |  | 60 | Seal Plan 11 + Plan 62. Plan 62 flush: water 0.5-1.0 LPM @ 1 kg/cm2. Make: Flowserve Sanmar. 2 seals per pump (DE and NDE or DS)
FLG-FLW-001 | Counter Flange Suction 14" PN16 FF | MS2425801-FLG-S | Flange | Counter Flange | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | EA | ASTM A105 |  | 45 | Slip-on type, Flat Face, 14" PN16. OD 520mm, BCD 470mm, 16 holes Ø26mm. Surface finish 125-250 AARH. Loose supplied by Flowserve
FLG-FLW-002 | Counter Flange Discharge 12" PN16 FF | MS2425801-FLG-D | Flange | Counter Flange | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | EA | ASTM A105 |  | 45 | Slip-on type, Flat Face, 12" PN16. OD 460mm, BCD 410mm, 12 holes Ø26mm, Thk 28mm. Loose supplied by Flowserve
GSK-FLW-001 | Gasket Full Face Non-Asbestos B16.21 3mm | MS2425801-GSK | Gasket | Flat Gasket | Flowserve 300-LNN-600 | Flowserve Corporation | 2 | EA | Non-Asbestos Flat Face |  | 30 | Full face type B16.21 std, 3mm thick. For suction & discharge flanges. Loose supplied by Flowserve
FST-FLW-001 | Flange Stud & Nut Set Suction 14" PN16 | MS2425801-STD-S | Fasteners | Stud & Nut | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | SET | ASTM A193 Gr B7 / A194 2H |  | 30 | 16 studs ASTM A193 Gr B7 + nuts ASTM A194 2H. Loose supplied by Flowserve
FST-FLW-002 | Flange Stud & Nut Set Discharge 12" PN16 | MS2425801-STD-D | Fasteners | Stud & Nut | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | SET | ASTM A193 Gr B7 / A194 2H |  | 30 | 12 studs ASTM A193 Gr B7 + nuts ASTM A194 2H. Loose supplied by Flowserve
CPL-FLW-001 | Coupling Spacer Tyre Type 300-LNN-600 | MS2425801-CPL | Coupling | Spacer Tyre | Flowserve 300-LNN-600 | Rathi Couplings | 1 | EA | Steel + Rubber Element | 50 | 45 | DBSE=250mm. Make: Rathi. Type: Spacer Tyre. Weight 50 kg from GA. Non-sparking aluminum coupling guard supplied by Flowserve
GRD-FLW-001 | Coupling Guard Non-Sparking Aluminum | MS2425801-GRD | Guard | Coupling Guard | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | EA | Aluminum (Non-Sparking) |  | 45 | Non-sparking aluminum coupling guard. Part of scope of supply: Flowserve Flowtech
MOT-FLW-001 | Motor CGL 550kW 690V 4-Pole VFD NG450 | CGL-2241805 | Motor | HV Induction Motor | Flowserve 300-LNN-600 | Crompton Greaves (CGL) | 1 | EA | Standard motor construction | 5300 | 60 | Make: CGL (Crompton Greaves Ltd). Rating: 550kW, 690V/3Ph/50Hz, 4-Pole, VFD driven. Frame: NG450. IC411 cooling. Speed range: 1143-1233 rpm. Work order 2241805. Motor enclosed in acoustic enclosure. 10% derating considered for 50°C ambient / 900m altitude. Efficiency ~94-95.5% at 60-100% load. PF ~0.27-0.87. LRC: 600% FLC. Starting time @100%V: 3sec
ENC-FLW-001 | Acoustic Enclosure for Motor 300-LNN-600 | ARK-ENC-2241805 | Enclosure | Acoustic Enclosure | Flowserve 300-LNN-600 | ARK Acoustics | 1 | EA | Steel Modular Panels | 2350 | 90 | Weight 2350 kg. Noise limit: 85 dBA combined. Modular panel design - selectively removable panels. Ceiling light provided. Roof slopes west for rainwater drainage. Air intake on 3 sides + exhaust duct. Clearance motor to enclosure top min 600mm. Coupling opening on enclosure. Loose supplied to site to avoid transport damage
BPL-FLW-001 | Baseplate IS2062 Drain Pan Type 300-LNN-600 | MS2425801-BP | Baseplate | Common Baseplate | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | EA | IS 2062 Mild Steel | 3250 | 60 | Weight 3250 kg. Drain pan + grouted type. Length 4800mm. 14 Nos M20 jacking bolts. 14 Nos Ø25 holes for foundation bolts (M20, HDG mild steel). 8 Nos motor alignment bolts. Grout: Shrinkkomp-30 or Fosroc Conbextra-GP2 (high strength non-shrink). API 610 Annex D tolerances
FBL-FLW-001 | Foundation Bolt Set 3/4" HDG MS | MS2425801-FB | Foundation | Foundation Bolts | Flowserve 300-LNN-600 | Flowserve Corporation | 14 | EA | Mild Steel with HDG |  | 30 | 14 Nos. Dia 3/4". Material: Mild Steel with Hot Dip Galvanizing. Primary concrete embedding type with loose washer. Flowserve scope of supply
PIP-FLW-001 | Plan 11 Piping Assembly | MS2425801-P11 | Piping | Seal Flush Piping | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | SET | ASTM A106 Gr B / A312 Gr 316L / A182 F316L |  | 45 | Plan 11 piping: 1/2" Sch 80 pipe (A106 Gr B), SS316L pipe (A312 Gr 316L), nipples, SWRF flanges (A105/A182 F316L), orifice plate (A240 Gr 316L). Connects casing (N1) to seal (N2)
ASM-FLW-001 | Complete Pump Package 300-LNN-600 | MS2425801-PKG | Assembly | Complete Package | Flowserve 300-LNN-600 | Flowserve Corporation | 1 | PKG | Various | 12160 |  | Total package weight ~12160 kg: Pump 1160 + Motor 5300 + Baseplate 3250 + Coupling 50 + Accessories 50 + Enclosure 2350. Scope: Bare pump + Mech seal + Coupling & guard + Motor & enclosure + Foundation bolts. Doc: MS2425801_001-68132-01 Rev 3
PUMP-WILO-GSN-T | Pump Assembly - Wilo 150-200-GSN 2-Stage (Taljhari) | GSN150-MC/12-P4-0-1480 | Pump | Centrifugal Horizontal HSC | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | Various (See Components) | 2175 |  | Taljhari ESR; 2-stage; Q=5060 LPM / 303.6 m3/h; H=150m; Speed=1489rpm; Eff=75.77%; Input=163.68kW; Motor=200kW; NPSHR=4.57m; Shutoff=171m; Min Cont Flow=1750 LPM; Total static load=2175 kg; IS 6595
CAS-WILO-GSN-001 | Pump Casing Top Half 150-200-GSN |  | Casing | Upper Casing | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | CI IS 210 Gr FG 260 |  |  | Axial split (horizontal split) casing; single volute; foot mount; Suction 200mm / Discharge 150mm; ANSI 125/150 FF flange drilling
CAS-WILO-GSN-002 | Pump Casing Bottom Half 150-200-GSN |  | Casing | Lower Casing | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | CI IS 210 Gr FG 260 |  |  | Bottom half of axial split casing; includes inter-stage collar CI and inter-stage ring CI
IMP-WILO-GSN-001 | Impeller 1st Stage (RH) 150-200-GSN |  | Impeller | Closed Impeller | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | Bronze LTB5 IS:318 |  |  | Item 1503 from cross section; 1st stage RH impeller; closed type; shaft mounted; max dia rated impeller
IMP-WILO-GSN-002 | Impeller 2nd Stage (LH) 150-200-GSN |  | Impeller | Closed Impeller | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | Bronze LTB5 IS:318 + Coating |  |  | Item 1504 from cross section; 2nd stage LH impeller; LTB5 with coating; 2-stage pump
SHAFT-WILO-GSN | Pump Shaft 150-200-GSN |  | Shaft | Pump Shaft | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | SS410 ASTM A276 Gr 410 |  |  | Item 1800 from cross section; solid shaft; shaft dia at coupling=90mm; CCW rotation from impeller end
SLEVE-WILO-GSN | Shaft Sleeve 150-200-GSN |  | Sleeve | Shaft Sleeve | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 2 | EA | SS410 ASTM A276 Gr 410 |  |  | Item 2100 from cross section; 2 nos; shaft sleeve under gland packing
SEAL-WILO-GSN | Gland Packing (Stuffing Box) 150-200-GSN |  | Seal | Gland Packing | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | SET | Graphited Cotton |  |  | Item 2410 from cross section; standard gland packing; stuffing box CI (item 2404); gland CI (item 2310); lantern ring GFN (item 2300)
BRG-WILO-GSN | Deep Groove Ball Bearing 6311 ZZ 150-200-GSN | 6311 ZZ | Bearing | Radial Ball Bearing | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 2 | EA | Steel |  |  | Item 2600 from cross section; 2 nos per pump; grease lubricated; bearing housing CI
WRNG-WILO-GSN | Casing Wear Ring / Neck Ring 150-200-GSN |  | Wear Ring | Casing Wear Ring | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 2 | EA | Bronze LTB5 IS:318 |  |  | Item 1181 neck ring from cross section; 2 nos; LTB5 bronze; casing wear rings
MOT-KECL-200 | Motor Kirloskar 200kW SA315M 415V Star-Delta | 32210424 | Motor | LT Induction Motor | Wilo 150-200-GSN (Taljhari) | Kirloskar Electric Company Ltd | 1 | EA | Cast Iron Frame | 1350 |  | KECL frame SA315M; 200kW; 415V±10% / 3Ph / 50Hz; 4-pole / 1500 rpm sync; Full load: 1484 rpm / 332A; IC01 cooling; IP23; Insul Class F / Temp rise limited to B; S1 duty; GD²=30 kgm²; PF full=0.90 / 3/4=0.89 / 1/2=0.84; Eff full=94% / 3/4=92.5% / 1/2=88%; LRC=6x DOL / 2x Y-Δ; Stall time cold/hot DOL: 89s/44s; DE brg 6319C3; NDE brg 6315C3; Paint RAL5010; Cable 2R x 3C x 240mm²; Star-Delta starter
BASE-WILO-GSN | Baseplate / Common Base Frame 150-200-GSN |  | Baseplate | Common Baseplate | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | MS Fabricated |  |  | Common base for pump + motor; baseplate length per GAD; ANSI 125/150 FF flange connections
ASM-WILO-GSN-T | Complete Pump Package 150-200-GSN (Taljhari) | 81343152/11 | Assembly | Complete Package | Wilo 150-200-GSN (Taljhari) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | PKG | Various | 2175 |  | Total static weight 2175 kg; Pump + motor package; Qty 2 pumps for Taljhari ESR; Customer: Sudhakara Infratech; End Customer: DW&S Div Sahibganj; IS 6595
PUMP-WILO-GSN-B | Pump Assembly - Wilo 150-200-GSN 2-Stage (Borio) | GSN150-MC/12-P4-0-1480 | Pump | Centrifugal Horizontal HSC | Wilo 150-200-GSN (Borio) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | Various (See Components) | 1823 |  | Borio ESR; 2-stage; Q=5170 LPM / 310.2 m3/h; H=143.83m; Speed=1488rpm; Eff=76.10%; Input=159.66kW; Motor=190kW (non-standard); Max head=166m; Min Cont Flow=1750 LPM; Total static load=1823 kg; Wilo SO 81343152/20
MOT-KECL-190 | Motor 190kW (Non-Standard) for Borio GSN Pump |  | Motor | LT Induction Motor | Wilo 150-200-GSN (Borio) | Kirloskar Electric Company Ltd | 1 | EA | Cast Iron Frame | 1250 |  | 190kW non-standard motor per Wilo data sheet; Weight approx 1250 kg; 4-pole / 1488 rpm; 415V; Note: non-standard rating flagged in datasheet
ASM-WILO-GSN-B | Complete Pump Package 150-200-GSN (Borio) | 81343152/20 | Assembly | Complete Package | Wilo 150-200-GSN (Borio) | Wilo Mather & Platt Pumps Pvt Ltd | 1 | PKG | Various | 1823 |  | Total static weight 1823 kg; Qty 2 pumps for Borio ESR; Customer: Sudhakara Infratech; End Customer: DW&S Div Sahibganj; IS 6595
PUMP-JYT-400TE3D4 | Pump Assembly - Jyoti 400TE3D4 (5-Stage VTP) | SP-PT25-P31722_3 | Pump | Vertical Turbine Pump | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 1 | EA | Various (See Components) | 5280 |  | MP Jal Nigam Pawai ¦ Q=10234 LPM / 614 m3/h; Bowl H=116m; Pump H=115.5m; Bowl Eff=84%; Pump Eff=83%; Bowl Power=230.93kW; Pump Power=231.68kW; Speed=1480rpm; 5-stage; Shutoff=154.29m (133%); Max Imp Ø327mm; Rated Imp Ø326mm; Min Imp Ø308mm; Specific Speed=2990.54 US; Vib max 4.5mm/s; Noise 85dB @1.85m; GD²=4.25 kgm²; Column 300x60mm; Discharge DS-300; Drawing GA/CS-2022
BOWL-JYT-400 | Bowl / Casing - Jyoti 400TE3D4 |  | Casing | Bowl / Stage Casing | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 5 | EA | SG Iron IS:1865 |  |  | Item 6 from BOM; 5 nos (one per stage); spheroidal graphite iron; includes top bowl (item 8) SG Iron
IMP-JYT-400 | Impeller - Jyoti 400TE3D4 (Per Stage) |  | Impeller | Closed Impeller | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 5 | EA | SSCF8M ASTM A743 |  |  | Item 5 from BOM; 5 nos (one per stage); SS CF8M stainless; closed type; Rated Ø326mm; Max Ø327mm; Min Ø308mm
SHAFT-JYT-400-IMP | Impeller Shaft - Jyoti 400TE3D4 |  | Shaft | Impeller Shaft | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 1 | EA | SS410T ASTM A276 |  |  | Item 9 from BOM; impeller shaft SS 410T ASTMA276
SHAFT-JYT-400-LINE | Line Shaft Assembly - Jyoti 400TE3D4 (per section) |  | Shaft | Line Shaft | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 12 | EA | SS410T ASTM A276 |  |  | Item 2 from BOM; 12 sections (1500mm each); column length 19200mm = 1500x12 + 1200x1; SS 410T ASTMA276; shaft dia 60mm NB
SHAFT-JYT-400-HEAD | Head Shaft - Jyoti 400TE3D4 |  | Shaft | Head Shaft | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 1 | EA | SS410T ASTM A276 |  |  | Item 1" from BOM; head shaft connecting motor to line shaft SS 410T ASTMA276
COLPIPE-JYT-400 | Column Pipe - Jyoti 400TE3D4 (per section) |  | Piping | Column Pipe | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 13 | EA | ERW Steel Pipe |  |  | Item 1 from BOM; 12x1500mm + 1x1200mm = 19200mm total column length; Ø300mm NB column pipe; ERW steel pipe
DHEAD-JYT-400 | Discharge Head Body DS-300 - Jyoti 400TE3D4 |  | Casing | Discharge Head | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 1 | EA | CI FG 200 IS:210 |  |  | Item 2" from BOM; discharge head body DS-300; square port opening 500x500; CI FG 200; discharge above floor; delivery flange OD Ø457mm; ID Ø300mm; PCD Ø406.4mm; 12 holes M20
BRG-JYT-400-LINE | Line Shaft Bearing (Thordon) - Jyoti 400TE3D4 |  | Bearing | Water Lubricated Bearing | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 12 | EA | Thordon Polymer |  |  | Item 4 from BOM; Thordon type; one per line shaft section; self-water lubricated; bearing holder CI FG 200
BRG-JYT-400-BUSH | Bush Bearing (Bowl) - Jyoti 400TE3D4 |  | Bearing | Bush Bearing | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 5 | EA | Bronze LTB2 IS:318 |  |  | Item 7 from BOM; 5 nos; bronze LTB2; bowl bearing; also suction case bearing bronze LTB2 (item 3)
WRNG-JYT-400 | Impeller Wearing Ring - Jyoti 400TE3D4 |  | Wear Ring | Impeller Wear Ring | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 5 | EA | Bronze LTB2 IS:318 |  |  | Item 4 from BOM; 5 nos (one per stage); bronze LTB2 IS:318
STRNR-JYT-400 | Strainer - Jyoti 400TE3D4 |  | Strainer | Suction Strainer | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 1 | EA | MS Fab IS:2062 |  |  | Item 1 from BOM; MS fabricated IS:2062; sump strainer; min submergence level 2.093m; sump clearances: side 385mm / back 288.75mm
SEAL-JYT-400 | Stuffing Box / Gland Packing - Jyoti 400TE3D4 |  | Seal | Gland Packing | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 1 | SET | CI FG 200 / Gland Packing STD |  |  | Item 5" stuffing box CI FG 200; item 4" stuffing box sealing gland packing STD; item 3" gland CI FG 200
CPL-JYT-400 | Line Shaft Coupling - Jyoti 400TE3D4 |  | Coupling | Shaft Coupling | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 12 | EA | SS410T ASTM A276 |  |  | Item 7 from BOM; SS 410T ASTMA276; connects line shaft sections; also impeller shaft coupling (item 11) and head shaft coupling (item 5)
MOT-JYT-400 | Motor 315kW CUD315 Solid Shaft VTP - Jyoti 400TE3D4 | P31722_3 | Motor | HV Induction Motor | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 1 | EA | Cast Iron Frame | 2800 |  | Frame CUD315; solid shaft type; 315kW / 425hp; 4-pole; 1480rpm; Motor weight 2800kg; Motor skirt MS Fab IS:2062 (item 7"); Motor coupling CI FG 200 (item 9"); Pump coupling CI FG 200 (item 8"); Soleplate MS Fab IS:2062 (item *); Foundation bolts: 4 Nos AM24x500mm (not in Jyoti scope); Static load: 79.26kN; Dynamic horiz @duty: 13.05kN; Dynamic vert @duty: 105.83kN
ASM-JYT-400TE3D4 | Complete Pump Package - Jyoti 400TE3D4 | SP-PT25-P31722_3 | Assembly | Complete Package | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | 1 | PKG | Various | 8080 |  | Total: Pump 5280kg + Motor 2800kg = 8080kg; 2 nos for MP Jal Nigam Pawai; Customer: Zetwerk; Report SP-PT25-P31722_3 Rev R0 dated 30-06-2025; Drawing GA/CS-2022
PUMP-JYT-350TE1A4 | Pump Assembly - Jyoti 350TE1A4 (7-Stage VTP) | SP-PT25-P31722/1 | Pump | Vertical Turbine Pump | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 1 | EA | Various (See Components) | 3350 |  | MP Jal Nigam Pawai ¦ Q=5117 LPM / 307 m3/h; Bowl H=116m; Pump H=115m; Bowl Eff=81%; Pump Eff=80%; Bowl Power=119.74kW; Pump Power=120.49kW; Speed=1480rpm; 7-stage; Shutoff=177.8m (153%); Max Imp Ø286mm; Rated Imp Ø279.9mm; Min Imp Ø256mm; Specific Speed=2713.69 US; Vib max 4.5mm/s; Noise 85dB @1.85m; GD²=1.015 kgm²; Column 200x50mm; Discharge DS-200; Drawing GA/CS-2021
BOWL-JYT-350 | Bowl / Casing - Jyoti 350TE1A4 |  | Casing | Bowl / Stage Casing | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 7 | EA | SG Iron IS:1865 |  |  | Item 6 from BOM; 7 nos (one per stage); spheroidal graphite iron; includes top bowl (item 8) SG Iron
IMP-JYT-350 | Impeller - Jyoti 350TE1A4 (Per Stage) |  | Impeller | Closed Impeller | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 7 | EA | SSCF8M ASTM A743 |  |  | Item 5 from BOM; 7 nos (one per stage); SS CF8M; closed type; Rated Ø279.9mm; Max Ø286mm; Min Ø256mm
SHAFT-JYT-350-IMP | Impeller Shaft - Jyoti 350TE1A4 |  | Shaft | Impeller Shaft | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 1 | EA | SS410T ASTM A276 |  |  | Item 9 from BOM; impeller shaft SS 410T ASTMA276; Ø350mm bowl diameter
SHAFT-JYT-350-LINE | Line Shaft Assembly - Jyoti 350TE1A4 (per section) |  | Shaft | Line Shaft | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 13 | EA | SS410T ASTM A276 |  |  | Item 2 from BOM; 12x1500mm + 1x1100mm = 19100mm total column; Ø50mm NB line shaft; SS 410T ASTMA276
COLPIPE-JYT-350 | Column Pipe - Jyoti 350TE1A4 (per section) |  | Piping | Column Pipe | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 13 | EA | ERW Steel Pipe |  |  | Item 1 from BOM; 12x1500mm + 1x1100mm = 19100mm total; Ø200mm NB column pipe; ERW steel pipe
DHEAD-JYT-350 | Discharge Head Body DS-200 - Jyoti 350TE1A4 |  | Casing | Discharge Head | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 1 | EA | CI FG 200 IS:210 |  |  | Item 2" from BOM; discharge head body DS-200; square port opening 410x410; CI FG 200; delivery flange OD Ø343mm; ID Ø200mm; PCD Ø292mm; 8 holes M16
MOT-JYT-350 | Motor 160kW CUTF315 Solid Shaft VTP - Jyoti 350TE1A4 | P31722/1 | Motor | LT Induction Motor | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 1 | EA | Cast Iron Frame | 1350 |  | Frame CUTF315 (IE-III); solid shaft type; 160kW / 215hp; 4-pole; 1480rpm; Motor weight 1350kg; Static load: 46.11kN; Dynamic horiz @duty: 9.98kN; Dynamic vert @duty: 88.26kN; Foundation bolts 4x AM24x500mm (not in Jyoti scope)
ASM-JYT-350TE1A4 | Complete Pump Package - Jyoti 350TE1A4 | SP-PT25-P31722/1 | Assembly | Complete Package | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | 1 | PKG | Various | 4700 |  | Total: Pump 3350kg + Motor 1350kg = 4700kg; 2 nos for MP Jal Nigam Pawai; Customer: Zetwerk; Report SP-PT25-P31722/1 Rev R0 dated 30-06-2025; Drawing GA/CS-2021
PUMP-WILO-MPS3 | Pump Assembly - Wilo MPS-3 1-Stage VTP | 81332087-10 GA | Pump | Vertical Turbine Pump | Wilo MPS-3 1-Stage VTP | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | Various (See Components) |  |  | Sauni Yojana Link-2 Package-9; FPS-8 Shell Dedumal; Q=68 m3/h; H=68m; Speed=1482rpm; Motor=260kW; VTP 1-stage; bore 450mm NB; antifriction oil lube; direction CW from top; Frame VPC710; Wilo SO 81332087; Base frame added per revision (8mm to 14mm thickness); column pipe 1200x3+1000x1=4600mm; delivery pipe 1500mm+1990mm
DHEAD-WILO-MPS3 | Discharge Head / Motor Stool MPS-3 |  | Casing | Discharge Head | Wilo MPS-3 1-Stage VTP | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | MS Fab / CI |  |  | From GAD 81332087-10; delivery pipe; 450mm bore; square port opening; plan view base frame 2100 CTC x 2200 SQ; coupling end detail 45mm bore; foundation bolt holes 16 Nos M30 drill
MOT-WILO-MPS3 | Motor 260kW VPC710 (Hollow/Solid Shaft) MPS-3 |  | Motor | LT/HT Induction Motor | Wilo MPS-3 1-Stage VTP | Wilo Mather & Platt Pumps Pvt Ltd | 1 | EA | Cast Iron Frame |  |  | From GAD 81332087-10; 260kW; frame VPC710; CGL make; 4-pole; antifriction oil lubricated; Motor stool connection; coupling end dimensions: pump shaft bore 45mm; motor shaft bore 100mm; coupling details per GAD
ASM-WILO-MPS3 | Complete Pump Package - Wilo MPS-3 VTP | 81332087-10 | Assembly | Complete Package | Wilo MPS-3 1-Stage VTP | Wilo Mather & Platt Pumps Pvt Ltd | 1 | PKG | Various |  |  | Sauni Yojana Link-2 Package-9; FPS-8 Shell Dedumal; approved by Bhavnagar Irrigation Project Division (Approval 9-35 dated 11/09/2023); TPI: Technomen Consultants; Drawing 81332087-10 GA Rev 03
PUMP-KSB-WKT809 | Pump Assembly - KSB WKT 80/9 Live Steam Condensate | 9975603447/300/400 | Pump | Vertical Turbine Pump VS6 | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | Various SS304 (See Components) | 1561 |  | NALCO Alumina Refinery Stream-5 ¦ Tags 08PU-J5821A/B & 08PU-K5821A/B ¦ Qty 4 (2 per unit J&K) ¦ Service: Live Steam Condensate ¦ Q=44.5 m3/h ¦ H=113.2m ¦ Speed=1480rpm ¦ BKW=24.26kW ¦ Motor=30kW ¦ Eff=75% ¦ Sealing: Plan 13+61 ¦ Direction: CCW from coupling end ¦ API 610 VS6 ¦ Double-casing diffuser inline suction/discharge
BOWL-KSB-WKT809 | Bowl Assembly - KSB WKT 80/9 |  | Casing | Bowl/Stage Casing | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | SS304 |  |  | Includes bowl shaft SS304, bowl SS304, suction bell SS304; double-casing diffuser type; bearing sleeve VTA; bowl wear ring VTA; O-ring VTA
IMP-KSB-WKT809 | Impeller - KSB WKT 80/9 |  | Impeller | Closed Impeller | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | SS304 |  |  | SS304; impeller dia VTA (min/max per vendor); closed type; condensate water service; temp 136°C rated / 148°C max
COL-KSB-WKT809 | Column Pipe Assembly - KSB WKT 80/9 |  | Piping | Column Assembly | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | SS304 / SS316 |  |  | Column pipe SS304; line shaft SS304; bearing retainer VTA; bearing sleeve (line shaft) VTA; shaft sleeve SS316; shaft coupling SS316; fasteners SS316
DHEAD-KSB-WKT809 | Discharge Head Assembly - KSB WKT 80/9 |  | Casing | Discharge Head | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | SS304 |  |  | Discharge head SS304; top shaft VTA; seat chamber/stuffing box assembly VTA; drain connection N8 NPT 1/2" plugged; vent connection N1 Adaptor NPT 3/4" KSB scope; inline suction and discharge nozzles per API 610 VS6
SEAL-KSB-WKT809 | Mechanical Seal + Plan 13+61 - KSB WKT 80/9 |  | Seal | Mechanical Seal | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | VTA |  |  | Mechanical seal; API Plan 13 (recirculation from mech seal through orifice to pump suction DN5) + Plan 61 (vent/inlet/drain NPT 1/2" plugged); flushing plan VTA; seal cooling plan VTA
STRNR-KSB-WKT809 | Suction Strainer (Start-up) - KSB WKT 80/9 |  | Strainer | Start-up Strainer | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | VTA |  |  | Start-up strainer type; body MOC VTA; strainer MOC VTA; mesh micron VTA; end connection flanged 125-250 AARH; KSB scope of supply
CPL-KSB-WKT809 | Coupling & Coupling Guard - KSB WKT 80/9 | REM 65-250 B/B | Coupling | Flexible Coupling | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | Steel/Rubber |  |  | Coupling REM 65-250 B/B; GD² of coupling = 0.013 kgm²; coupling guard included; flexible coupling with spacer type; KSB scope
MOT-ABB-30KW-WKT | Motor ABB 30kW Frame 225 M 415V 1480rpm |  | Motor | LT Induction Motor | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | Cast Iron Frame | 171 |  | Make: ABB; Frame size: 225 M; 30kW; 415V/3Ph/50Hz; 1440/1480rpm; Weight motor=171kg; Weight pump barrel+column pipe=1390kg; Motor lantern+base frame+coupling=~170kg approx; GD²pump=0.2454 kgm²; Total weight=1561kg; Direction CCW from coupling end; TEFC enclosure; ambient 50°C; squirrel cage
BASE-KSB-WKT809 | Motor Lantern + Base Frame + Mounting Plate - KSB WKT 80/9 |  | Baseplate | Motor Lantern/Base Frame | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | Mild Steel Fabricated |  |  | Motor lantern + base frame + coupling included in scope; base frame pad welded on channel (KSB scope); barrel top plate KSB scope; square base frame channel IS MC 200; mounting plate by KSB; fixing stud M20x70 LG; FFL +930.300m; concrete block by others
FLG-KSB-WKT809-D | Counter Flange Discharge CL150 RF - KSB WKT 80/9 |  | Flange | Counter Flange | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | ASTM A216 WCB |  |  | Discharge counter flange DN100; CL150 RF; OD 229mm; PCD 190.5mm; Thk 23.9mm; 8 holes Ø19mm; ASME B16.5-250 AARH; loose supplied; nozzle loads: Fx=200N, Fy=260N, Fz=200N; Mx=150Nm, My=150Nm, Mz=150Nm
FLG-KSB-WKT809-S | Counter Flange Suction CL150 RF - KSB WKT 80/9 |  | Flange | Counter Flange | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | EA | ASTM A216 WCB |  |  | Suction counter flange DN150; CL150 RF; OD 279mm; PCD 241.3mm; Thk 25.4mm; 8 holes Ø22mm; ASME B16.5-250 AARH; loose supplied
ASM-KSB-WKT809 | Complete Pump Package - KSB WKT 80/9 | 9975603447/300 | Assembly | Complete Package | KSB WKT 80/9 (Live Steam Condensate) | KSB Limited (India) | 1 | PKG | Various | 1561 |  | Total weight 1561kg: Motor 171kg + Pump barrel+column 1390kg; Scope: pump+mech seal+Plan13+coupling+guard+motor+motor stool+base frame+suction/discharge counter flanges; Dynamic load per foundation bolt=80kgf; Static load per foundation bolt=84.5kgf; Connections N1(vent) N2(N/A) N3(plan13) N8(drain); Document F9975603447-300-1 As Built; Client PO ZET-OD-KSB2-1 DT.19/10/2024
PUMP-KSB-STGC | Pump Assembly - KSB STGC 050-160-CC-WDL Acid Sump | 9975641078/0100 | Pump | Vertical Sump Pump VS6 | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB Limited (India) | 1 | EA | Various (See Components) | 193 |  | NALCO Alumina Refinery Stream-5 ¦ Tag 08PU-J5893 ¦ Qty 1 ¦ Service: Dilute Sulphuric Acid Sump ¦ Q=80 m3/h rated ¦ H=30m ¦ Speed=2940rpm ¦ Motor=15kW ¦ Weight pump empty=193kg; pump operating=243kg ¦ FFL+930.300m; tank EL+928.290m; mounting plate by KSB; KSB S.O. 9975641078/0100; ZW drawing ZT2023.02-508-GA-ME-241; Client PO ZET-OD-KSB2-2 dt 09.12.2024
IMP-KSB-STGC | Impeller - KSB STGC 050-160-CC-WDL |  | Impeller | Closed Impeller | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB Limited (India) | 1 | EA | MOC per KSB (acid service) |  |  | Suitable for dilute sulphuric acid service; impeller dia VTA; closed type; 2940rpm high speed pump
SEAL-KSB-STGC | Mechanical Seal - KSB STGC 050-160-CC-WDL |  | Seal | Mechanical Seal | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB Limited (India) | 1 | EA | Acid-resistant MOC |  |  | Mechanical seal for dilute sulphuric acid service; seal plan VTA; KSB scope
CPL-KSB-STGC | Coupling & Guard - KSB STGC 050-160-CC-WDL | RB (RATHI) | Coupling | Flexible Coupling | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB Limited (India) | 1 | EA | Steel/Rubber |  |  | Coupling RB (Rathi); GD² pump=0.0434 kgm²; dynamic load per fixing bolt=3162 kgf; coupling guard KSB scope; 4 Nos M16 fixing bolts KSB scope
MOT-ABB-15KW-STGC | Motor ABB 15kW Frame 160M 415V 2940rpm IE3 |  | Motor | LT Induction Motor | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | ABB India Ltd | 1 | EA | Cast Iron Frame | 126 |  | Make: ABB; Frame: 160M; 15kW; 2940rpm; TEFC IE3; Weight=126kg; Cable box position VTA; Clockwise rotation from DE; pump shaft end bore Ø24mm; motor shaft end bore Ø45mm; fixation holes Ø20; pump shaft end dim: 40-27-6-42-12; motor shaft end dim: 40-45-12; overall pump+motor height=2023mm (without motor)=1033mm; 4 Nos M16x200 fixing bolts Ø20 hole on mounting plate
BASE-KSB-STGC | Mounting Plate & Hardware - KSB STGC 050-160-CC-WDL |  | Baseplate | Mounting Plate | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB Limited (India) | 1 | EA | Steel |  |  | Mounting plate by KSB; 4 Nos M16 fixing bolts KSB scope; Ø20 holes on mounting plate; hardware M20 MOC 4.6+A2A; PC Ø300mm; top flange of motor lantern Ø350mm; min liquid level 240mm; tank thickness 10mm; installation depth from FFL to tank bottom=1973mm; height HL to LL=700mm
FLG-KSB-STGC-D | Discharge Flange DN65 - KSB STGC 050-160-CC-WDL |  | Flange | Discharge Nozzle | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB Limited (India) | 1 | EA | KSB Standard |  |  | Discharge nozzle DN65; flange drilling per ASME B16.5; OD=178mm; PCD=139.7mm; BCD=184.7mm; 4 holes Ø19; forces: Fy=893N, Fz=1103N, Fx=971N; moments: My=420Nm, Mz=490Nm, Mx=700Nm
STRNR-KSB-STGC | Pump Suction Strainer - KSB STGC 050-160-CC-WDL |  | Strainer | Suction Strainer | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB Limited (India) | 1 | EA | Acid-resistant MOC |  |  | Suction strainer KSB scope; min overhead clearance with motor=2806mm; without motor=2221mm; pump installation depth 1973mm from FFL
ASM-KSB-STGC | Complete Pump Package - KSB STGC 050-160-CC-WDL | 9975641078/0100 | Assembly | Complete Package | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB Limited (India) | 1 | PKG | Various | 319 |  | Total weight 319kg: Pump empty 193kg + Operating 243kg + Motor 126kg; Scope: pump+suction strainer+coupling+coupling guard+motor+mounting plate+gasket+hardware+Ø20 fixing bolt M16x200; Document F9975641078-1 R5; ZW Drawing ZT2023.02-508-GA-ME-241
PUMP-KSB-PC5813 | Pump Assembly - KSB VS6 Process Condensate (DS-ME-115) | ZT2023.02-508-DS-ME-115 | Pump | Vertical Turbine Pump VS6 | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | EA | Various CS/SS (See Components) |  |  | NALCO Alumina Refinery Stream-5 ¦ Tags 08PU-J5813A/B & 08PU-K5813A/B ¦ Qty 4 (2 per unit J&K) ¦ Service: Process Condensate ¦ Q rated=172 m3/h; H rated=74.3m ¦ Temp=47°C ¦ Density=990 kg/m3 ¦ Viscosity=0.6 mPa.s ¦ VP=10 kPa(a) ¦ Inlet pressure=-74 to -76 kPa(g) ¦ NPSHA=0.5m ¦ Speed=1450rpm ¦ Motor=VTA(squirrel cage, 415V, 4-pole) ¦ Noise ≤85 dB(A) ¦ VSD driven (VSD by purchaser) ¦ API 610 VS6 or equivalent ¦ Doc ZT2023.02-508-DS-ME-115 Rev 3
CAS-KSB-PC5813 | Casing Assembly (Suction/Stage/Discharge) - KSB VS6 PC |  | Casing | Multi-Stage Casing | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | SET | CS ASTM A216 Gr WCB |  |  | Suction casing CS ASTM A216 Gr WCB; Stage casing CS ASTM A216 Gr WCB; Discharge casing CS ASTM A216 Gr WCB; diffuser VTA; casing test pressure VTA; double-casing inline suction/discharge; no of stages VTA
IMP-KSB-PC5813 | Impeller - KSB VS6 Process Condensate |  | Impeller | Closed Impeller | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | EA | SS 2324 (Lean Duplex) |  |  | SS 2324 lean duplex stainless steel; impeller dia VTA (min/max per vendor); closed type; impeller wear ring VTA; case wear ring VTA; process condensate 47°C service
SHAFT-KSB-PC5813 | Shaft & Sleeve - KSB VS6 Process Condensate |  | Shaft | Pump Shaft | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | EA | VTA |  |  | Shaft MOC VTA; shaft sleeve VTA; bearing housing VTA; stuffing box VTA; gland/seal plate VTA; bearings VTA; lubrication VTA; thrust balancing VTA
SEAL-KSB-PC5813 | Mechanical Seal - KSB VS6 Process Condensate |  | Seal | Mechanical Seal | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | EA | VTA |  |  | Mechanical seal; seal flushing plan VTA (vendor to advise); cooling plan VTA; condensate water service; NPSHA=0.5m (very low — VS6 required specifically for this)
CPL-KSB-PC5813 | Coupling & Guard - KSB VS6 Process Condensate |  | Coupling | Flexible Coupling with Spacer | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | EA | VTA |  |  | Flexible coupling with spacer; make VTA; size VTA; GD² of pump and coupling VTA; coupling guard included; KSB scope
MOT-KSB-PC5813 | Motor (Squirrel Cage) - KSB VS6 Process Condensate |  | Motor | LT Induction Motor | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | EA | Cast Iron Frame |  |  | Squirrel cage induction motor; nominal power VTA; 4-pole; 1450 rpm nom; 415V±10%/50Hz/3Ph; ambient 50°C; motor by pump vendor; driven through VSD (VSD by purchaser); motor per doc 6695-ELT-G00-EC-0012
BASE-KSB-PC5813 | Common Base Frame - KSB VS6 Process Condensate |  | Baseplate | Common Baseplate | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | EA | Carbon Steel |  |  | CS base frame; anchor bolts yes (vendor to provide details); base plate VTA; coupling halves VTA; mounted on common base frame with motor; includes companion flanges with gaskets and fasteners; foundation bolts in scope
STRNR-KSB-PC5813 | Suction Strainer (Start-up) - KSB VS6 Process Condensate |  | Strainer | Start-up Strainer | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | EA | VTA |  |  | Start-up strainer type; body MOC VTA; strainer MOC VTA; mesh micron VTA; end connection flanged 125-250 AARH; KSB scope of supply
ASM-KSB-PC5813 | Complete Pump Package - KSB VS6 Process Condensate | ZT2023.02-508-DS-ME-115 | Assembly | Complete Package | KSB VS6 Process Condensate Pump | KSB Limited (India) | 1 | PKG | Various |  |  | Scope: Pump+Motor+Common Base Frame+Coupling+Coupling Guard+Companion Flanges+Gaskets+Fasteners+Foundation Bolts+Suction Strainer+Mechanical Seal+First Fill Lubricants ¦ NO valves ¦ Operating points: MinFlow 99 m3/h @73.2m / Normal 141 m3/h @73.7m / MaxFlow 198 m3/h @75m ¦ Inlet press -74 to -76 kPa(g) ¦ Condensate pot tag 08PV-J/K-5813 ¦ Painting per 6695-EQS-G00-EC-0007 ¦ Noise ≤85 dB(A)

## Material_Database
Material_Code | Material_Description | Density_kg_m3 | Max_Temp_C | Standard_Spec | Typical_Applications | Notes
A216-WCB | Carbon Steel Casting WCB | 7850 | 425 | ASTM A216 | Pump casings, pressure vessels | Standard carbon steel for pump casings
A487-CA6M | 12% Chrome Steel Casting | 7700 | 450 | ASTM A487 Gr CA6M | Impellers, wear rings, high wear parts | Corrosion and wear resistant
CF8M-SS316 | Stainless Steel 316 Cast | 8000 | 538 | CF8M (ASTM A743) | Impellers, corrosive service | Excellent corrosion resistance
EN19-STEEL | Alloy Steel EN19 | 7850 | 400 | EN19 / SAE 4140 | Shafts, high strength applications | High tensile strength
SS410 | Stainless Steel 410 | 7750 | 400 | AISI 410 | Shafts, fasteners | Martensitic stainless steel
A216-TYPE420 | Stainless Steel 420 | 7740 | 400 | ASTM A216 Type 420 | Shaft sleeves, wear parts | Hardenable stainless
A48-CI30 | Cast Iron Class 30 | 7200 | 230 | ASTM A48 CI.30 | Bearing housings, low pressure | Standard gray cast iron
IS2062 | Mild Steel Structural | 7850 | 350 | IS 2062 | Baseplates, structural supports | Indian standard structural steel
A193-B7 | Alloy Steel Bolting | 7850 | 540 | ASTM A193 Gr.B7 | High temperature bolts | For bolted connections
A194-2H | Heavy Hex Nuts | 7850 | 540 | ASTM A194 2H | Nuts for A193 B7 bolts | Heavy duty nuts
SS304 | Stainless Steel 304 | 8000 | 870 | AISI 304 | Guards, nameplates, general fabrication | General purpose stainless
CARBON-STEEL | Carbon Steel General | 7850 | 400 | Various | Piping, structural, general fabrication | Generic carbon steel
ASTM-A532-IIIA | High Chrome White Iron (GPS800 equiv.) | 7200 | 400 | ASTM A532 Grade IIIA | Pump casings, impellers, back liners - slurry service | Metso internal code GPS800; wear resistant
SS316-CAST | Stainless Steel 316 (Wrought) | 8000 | 400 | SS316 / 1.4436 | Shaft sleeves | Corrosion resistant shaft sleeve
EN24-STEEL | EN24 Alloy Steel (BS970) | 7850 | 450 | EN24 / BS970 | Pump shafts | High tensile alloy steel for shafts
SG-IRON-500 | Spheroidal Graphite (SG) Iron GR.500/7 | 7100 | 350 | BS2789 Gr.500/7 | Bearing housing | Ductile iron for bearing housings
IS2062-MS | Structural Mild Steel IS:2062 | 7850 | 300 | IS 2062 | Bearing frame, base frame | Standard structural steel
NBR-70 | Nitrile Rubber 70 Shore |  | 100 | NBR 70 SH | O-rings, gaskets | SMS1586 spec o-rings
PVC-U | Unplasticised PVC |  | 60 | PVC-U | Case shim modules | Non-metallic shim material
CI-FG260 | Cast Iron FG 260 | 7200 | 250 | IS 210 Gr FG 260 | Pump casings (horizontal split), bearing housings, glands, suction cases | Standard CI for water pumps; Wilo GSN casing & Jyoti VTP discharge head body
BRONZE-LTB2 | Phosphor Bronze LTB2 | 8800 | 200 | IS 318 Gr LTB2 | Bush bearings, impeller wearing rings, bowl bearings, suction case bearings | Standard bronze for water pump wear parts; Jyoti VTP & Wilo GSN
BRONZE-LTB5 | Phosphor Bronze LTB5 | 8800 | 200 | IS 318 Gr LTB5 | Impellers in water pumps, casing wear rings | Higher grade bronze for impellers; Wilo GSN 2-stage pump
SG-IRON | Spheroidal Graphite (SG) Iron | 7100 | 300 | IS 1865 | Bowl / casing for vertical turbine pumps | Jyoti VTP bowl and top bowl material; ductile iron
SS410-BAR | Stainless Steel 410 (Bar/Rod) | 7750 | 400 | ASTM A276 Gr 410 | Impeller shafts, line shafts, head shafts, shaft couplings for VTPs | SS 410T ASTMA276; Used in Jyoti 400TE3D4 & 350TE1A4 shaft system
ERW-PIPE | ERW Steel Pipe (Column Pipe) | 7850 | 300 | IS 1239 / IS 3589 | Column pipes for vertical turbine pumps | Jyoti VTP column pipe material; Electric Resistance Welded steel pipe
THORDON | Thordon Bearing Material (Polymer) | 1200 | 80 | Thordon Proprietary | Line shaft bearings / water lubricated bearings in VTPs | Water-lubricated bearing; Jyoti VTP line shaft bearing; self-water lubricated
GFN | Glass Filled Nylon | 1400 | 100 | Manufacturer Std | Lantern rings in stuffing boxes | Wilo GSN pump lantern ring material
GRAPHITED-COTTON | Graphited Cotton Gland Packing | 1000 | 200 | Manufacturer Std | Gland packing / stuffing box sealing | Standard gland packing; Wilo GSN & Jyoti VTP stuffing box

## Vendor_Database
Vendor_ID | Vendor_Name | Category | Location | Avg_Lead_Days | Notes
V-001 | Flowserve Corporation | Pump OEM | Global |  | Complete pump packages
V-002 | KSB Pumps Ltd | Pump OEM | India |  | Vertical and horizontal pumps
V-003 | Crompton Greaves (CGL) | Motors | India |  | 550kW motor supplier for Flowserve
V-004 | Laxmi Hydraulics Pvt Ltd | Motors | India | 0 | Motor supplier for KSB pumps
V-005 | Unique Transmission India | Couplings | India | 45 | Flexible couplings
V-006 | Rathi Couplings | Couplings | India |  | Spacer tyre type couplings
V-007 | John Crane Sealing Systems | Seals | India | 38 | Mechanical seals
V-008 | Flowserve Sanmar | Seals | India |  | Mechanical seals for Flowserve pumps
V-009 | Jsons Foundry Pvt Ltd | Castings | India | 21 | Pump castings and forgings
V-010 | KSB Pumps Foundries | Castings | India | 21 | Impeller castings
V-011 | Swaraj Engineering | Fabrication | India | 28 | Structural fabrication, piping
V-012 | J.J. Engineers | Fabrication | India | 50 | Baseplates and structures
V-013 | The Sky Industries | Fabrication | India | 50 | Fabricated components
V-014 | Sai Technofab | Fabrication | India | 30 | Guards and safety equipment
V-015 | Jay-Eesh Engineering Company | Piping Components | India | 35 | Strainers and piping
V-016 | ARK Acoustics | Acoustic Enclosures | India |  | Noise reduction enclosures
V-017 | Stock / Local Suppliers | General | India | 0 | Standard off-the-shelf items
V-018 | Metso Outotec India Pvt Ltd | Pump OEM / Slurry | Alwar, Rajasthan, India |  | HM200 slurry pump series manufacturer
V-019 | Innomotics India Pvt Ltd (formerly Siemens Large Drives) | Motors | Navi Mumbai, India |  | 500kW HV motors, IEC400 frame, VFD suitable
V-020 | Flowserve SANMAR Ltd | Mechanical Seals | Chennai, India |  | Mechanical seal supplier - model 2H-104764
V-021 | TIMKEN | Bearings | Global / India |  | Taper roller bearing supplier for pump FR500 bearing frame
V-022 | Fenner | Power Transmission | India |  | V-belt pulley and belt supplier (8V series)
V-023 | Wilo Mather & Platt Pumps Pvt Ltd | Pump OEM | Pune, Maharashtra, India |  | Horizontal split casing & VTP pumps; GSN series & MPS series; Taljhari/Borio/Sauni Yojana projects
V-024 | Jyoti Ltd | Pump OEM / VTP | Vadodara, Gujarat, India |  | Vertical Turbine Pumps; 400TE3D4 & 350TE1A4; MP Jal Nigam Pawai project; Customer: Zetwerk
V-025 | Kirloskar Electric Company Ltd | Motors | Bangalore/Hubli, India |  | LT AC motors; 200kW SA315M frame; Star-Delta start; For Wilo pump packages
V-026 | Sudhakara Infratech Private Limited | LSTK Contractor | India |  | LSTK contractor for Taljhari & Borio RWS scheme, Sahibganj
V-027 | ABB India Ltd | Motors | India |  | 15kW IE3 TEFC motor Frame 160M; 2940rpm; for KSB STGC sump pump
V-028 | KSB Limited (India) | Pump OEM | India |  | KSB WKT & STGC condensate/sump pumps; VS6 type; NALCO project

## Pump_Master_List
Pump_ID | Model | Manufacturer | Type | Flow_m3h | Head_m | Power_kW | Speed_rpm | Weight_kg | Motor_kW | Project
FLW-001 | Flowserve 300-LNN-600 | Flowserve | Horizontal | 961 | 86 | 347 | 1450 | 1160 | 550 | NALCO Alumina Refinery
KSB-001 | KSB RPH-V 50-360 | KSB | Vertical | 40 | 120 | 37.05 | 1450 | 410 | 45 | IOCL LOBS (3 units)
KSB-002 | KSB RPH-V 40-180 | KSB | Vertical |  |  |  |  | 350 | 5.5 | IOCL LOBS (1 unit)
METSO-001 | Metso HM200 MHC-S C5 DDE | Metso Outotec | Horizontal Slurry | 1140 | 78 | 366.8 | 1473 | 1010 | 500 | NALCO Alumina Refinery Stream-5 (Evaporation Unit J & K)
WILO-001 | Wilo 150-200-GSN (2-Stage) | Wilo Mather & Platt | Horizontal Split Casing | 303.6 | 150 | 163.68 | 1489 | 2175 | 200 | Taljhari & Borio RWS Scheme, DW&S Sahibganj ¦ Wilo SO 81343152/11 ¦ ESR Taljhari ¦ Clear Water
WILO-002 | Wilo 150-200-GSN (2-Stage) Borio | Wilo Mather & Platt | Horizontal Split Casing | 310.2 | 143.83 | 159.66 | 1488 | 1823 | 190 | Taljhari & Borio RWS Scheme, DW&S Sahibganj ¦ Wilo SO 81343152/20 ¦ ESR Borio ¦ Clear Water
JYOTI-001 | Jyoti 400TE3D4 (5-Stage VTP) | Jyoti Ltd | Vertical Turbine Pump | 614.04 | 116 | 231.68 | 1480 | 5280 | 315 | MP Jal Nigam Pawai Project ¦ Zetwerk ¦ Report SP-PT25-P31722_3 ¦ 5-stage ¦ 2 nos ¦ Water Supply
JYOTI-002 | Jyoti 350TE1A4 (7-Stage VTP) | Jyoti Ltd | Vertical Turbine Pump | 307.02 | 116 | 120.49 | 1480 | 3350 | 160 | MP Jal Nigam Pawai Project ¦ Zetwerk ¦ Report SP-PT25-P31722/1 ¦ 7-stage ¦ 2 nos ¦ Water Supply
WILO-003 | Wilo MPS-3 1-Stage VTP | Wilo Mather & Platt | Vertical Turbine Pump | 68 | 68 |  | 1482 |  | 260 | Sauni Yojana Link-2 Package-9 ¦ Zetwerk ¦ GAD 81332087-10 ¦ 1-stage ¦ FPS-8 Shell Dedumal ¦ Water Supply
KSB-003 | KSB WKT 80/9 (Live Steam Condensate) | KSB | Vertical Turbine Pump VS6 | 44.5 | 113.2 | 24.26 | 1480 | 1561 | 30 | NALCO Alumina Refinery Stream-5 ¦ Tags 08PU-J5821A/B & 08PU-K5821A/B ¦ KSB Order 9975603447/300 ¦ Live Steam Condensate ¦ Evap Unit J&K ¦ 4 Nos ¦ DS-ME-114
KSB-004 | KSB STGC 050-160-CC-WDL (Dilute Acid Sump) | KSB | Vertical Sump Pump VS6 | 80 | 30 |  | 2940 | 319 | 15 | NALCO Alumina Refinery Stream-5 ¦ Tag 08PU-J5893 ¦ KSB Order 9975641078/0100 ¦ Dilute Sulphuric Acid Sump ¦ Evaporation Unit ¦ 1 No ¦ F9975641078-1 R5
KSB-005 | KSB VS6 Process Condensate Pump | KSB | Vertical Turbine Pump VS6 | 172 | 74.3 |  | 1450 |  |  | NALCO Alumina Refinery Stream-5 ¦ Tags 08PU-J5813A/B & 08PU-K5813A/B ¦ Process Condensate ¦ Evap Unit J&K ¦ 4 Nos ¦ DS-ME-115 ¦ CS WCB casing, SS2324 impeller

## HM200_Dissection_Summary
PUMP DISSECTION SUMMARY
Model: | Metso HM200 MHC-S C5 DDE |  | Project: | NALCO 1.0 MTPA Alumina Refinery Stream-5
Tag Nos: | 08PU-J5801 A/B; 08PU-K5801 A/B (4 units total) |  | Service: | Feed Liquor Booster Pump
Manufacturer: | Metso Outotec India Pvt. Ltd. (Alwar) |  | Fluid: | Caustic Liquor (Aluminium Liquor)
Doc Ref: | OG05Z-EQP-508-DZ-0002-002 Rev 9 |  | Date Extracted: | 2025-02-24
PUMP PERFORMANCE DATA
Parameter | Min Flow | Normal | Rated | Max (BKW) | Units
Speed | 934 | 1221 | 1473 | 1473 | rpm
Flow | 650 | 929 | 1140 | 1173 | m³/h
Slurry Head | 33 | 54 | 78 | 79 | m
Pump Power (Slurry) | 89.4 | 207.7 | 366.8 | 382.7 | kW
Efficiency | 81.3% | 81.9% | 82.2% | 82.1% | %
Shutoff Head | 40.6 | 69.4 | 101.1 | 103.4 | m
Seal Arrangement | Mech. Seal | Mech. Seal | Mech. Seal | Mech. Seal
OPERATING CONDITIONS
Fluid | Caustic Liquor (Alumina/Aluminium Oxide)
Density | 1244 kg/m³ |  | Viscosity | 1.7 mPa.s
Op. Temperature | 79°C (max 100°C slurry) |  | Vapour Pressure | 33 kPa(a)
Inlet Pressure (Normal) | 337 kPa(g) |  | NPSHA | >15 m
NPSHR | 13.8 m |  | Min. Allowable Flow | 850 m³/h
Electrical data
Motor type - Squirrel Cage
MATERIAL OF CONSTRUCTION
Component | Material | Standard/Spec | Notes
Casing / Impeller / Back Liner | High Chrome White Iron | ASTM A532 GR.IIIA (GPS800) | Metso internal code GPS800
Shaft | EN24 Alloy Steel | BS970 | High tensile
Shaft Sleeve | Stainless Steel 316 | 1.4436 | Under seal
Bearing Frame | Mild Steel IS:2062 | E250BR
Bearing Housing | SG Iron GR.500/7 | BS2789
Casing Bolts | A197 2H & A192B7 | ASTM
O-Rings / Gaskets | NBR 70 Shore | SMS1586 | NR 70° SH
WEIGHTS (FROM GA DRAWING SAL537200)
Component | Weight (kg)
Pump (bare) | 1010
Motor (Innomotics 500kW) | 3400
V-Belt Guard | 107
Bed Frame with Motor Support | 792
TOTAL ASSEMBLY WEIGHT | 5390
MOTOR DATA (Innomotics 1LA4400-4AW00-Z)
Rated Power | 500 kW |  | Frame | IEC400
Voltage | 690 V |  | Poles | 4
Frequency | 50 Hz |  | Rated Speed | 1491 rpm
Rated Current | 570 A |  | Rated Torque | 3203 Nm
Power Factor | 0.78 |  | Efficiency @100% | 94.6%
IP Rating | IP55 |  | Cooling | IC411
Insulation Class | F (design) / B (utilization) |  | Duty | S1 Continuous
GD2 (Motor) | 11.6 kgm² |  | GD2 (Pump) | 5.08 kgm²
DE Bearing | SKF NU328E (grease) |  | NDE Bearing | SKF 6224C3 Insulated (grease)
DRIVE DETAILS
Drive Type | V-Belt (not direct coupled)
V-Belt | 10 x 8V-1600 (4060mm length)
Motor Pulley | 500mm PCD, 10G x 8V, Bush 5050/D110
Pump Pulley | 500mm PCD, 10G x 8V, Bush 5050/D80
MECHANICAL SEAL (Flowserve SANMAR)
Seal Model | 2H-104764 (Single Cartridge) |  | Plan | API Plan 62 + SLD
Seal Part No. | AX03-900016694 |  | Size | 5.875"
Seal Type | Single mech seal with SLD (Synthetic Lubricating Device)
PUMP EXPANDED PARTS LIST (from Metso dwg SAL537198)
Item | Part No. | Description | Material | Mass (kg) | Qty
1 | SAL534463-P1 | Frame Assembly (Frame Module FR500) | MS TZN | 205.4 | 1
2 | PDWB062-S | Bearing Assembly FR500-S DDE | Steel | 145.9 | 1
3 | SAL532662-W1 | Casing Module HM200 C5/W9 GPS800 | A532-IIIA + NBR | 375.1 | 1
3.1 | PDCH2034 | Case HM200 GPS800 | A532-IIIA | 321.2 | 1
3.2 | PDCH2021 | Back Liner FR500 GPS800 | A532-IIIA | 53.9 | 1
3.3 | SA959120 | O-Ring 350x5 NBR | NBR | 0 | 1
4 | SAL535831-P1 | Case Shim Module FR500-S PVC | PVC-U | 0.2 | 0
5 | PDCH2019 | Pump Impeller HM200 C5 GPS800 | A532-IIIA | 130.2 | 1
5.1 | PDCH2019-01 | Billet Impeller HM200 C5 GPS800 | A532-IIIA | 130.7 | 1
6 | AX03-900016694 | Mechanical Seal Single FR500 with Adaptor | Various | 34.9 | 1
7 | PDCH5050 | Shaft Sleeve FR500 | SS316 1.4436 | 4.4 | 1
8 | SA953201 | O-Ring SMS1586-99.50x3.00-NBR70 | NBR | 0 | 2
9 | ZX90010660 | Mechanical Seal Sticker | - | 0 | 1
10 | SAL530154-M1 | Gland Guard Kit FR500 | Steel | 1.4 | 1
11 | SAL535225-W1 | Wet End Fasteners Assembly HM200 | Steel TZN | 8.3 | 1
12 | 504079-M1 | Flange Assembly NPS 8" ANSI 300LB | Carbon Steel 1.0045 | 27.3 | 1
13 | PD731032 | Gasket Inlet/Outlet NR 70°SH NRB | NBR | 0.1 | 1
14 | 500680-M1 | Flange Assembly NPS 6"/150 ANSI 300 | Carbon Steel 1.0045 | 11.4 | 1
15 | PD701032 | Gasket Inlet/Outlet NR 70°SH NRB | NBR | 0.1 | 1
16 | 500125-S1-IN | Sign Kit Right Rotating Pump FR250 | - | 0 | 1

## ProdLiquor_300LNN600_Summary
DISSECTION SUMMARY — FLOWSERVE 300-LNN-600 PRODUCT LIQUOR PUMP
Project: NALCO 1.0 MTPA Alumina Refinery Stream-5 ¦ Doc: OG05Z-EQM-508-TB-0001 Rev 1 / MS2425801_001-68132-01 Rev 3 ¦ LSTK: Zetwerk ¦ Tech Partner: Metso Outotec
PUMP IDENTITY
Pump Model | 300-LNN-600
Manufacturer | Flowserve Corporation (Flowtech Engineers - Authorized Agent)
Service | Product Liquor Pump (Caustic Liquor — Alumina Process)
Tag Numbers | 08PU-J5802A/B & 08PU-K5802A/B
Quantity | 4 Nos. (2 each for Evaporation Units J & K)
Sales Order | MS2425801
Customer PO | PO-ZMBPL-FSG-RP-2024-25-123 & 29-OCT-24
Plant Location | NALCO, Damanjodi, Odisha ¦ Elevation: 900m ASL ¦ Outdoor
Type | Horizontal, Single Stage, Between-Bearings, Horizontally Split Casing
Standard | API 610
Direction | CCW viewed from NDE
Serial Numbers | 08PU-J5802A: 2324002 ¦ 08PU-J5802B: 2324003 ¦ 08PU-K5802A: 2324004 ¦ 08PU-K5802B: 2324005
PUMP PERFORMANCE (NAMEPLATE)
Parameter | Value |  | Parameter | Value
Flow (Q) | 961 m³/h |  | Head (H) | 86 m
Speed Range | 1143 to 1233 rpm (VFD) |  | Test Pressure | 24 barg
Impeller | Trimmed per performance |  | RPM (Nameplate) | 51.5 rpm [VFD]
Suction Nozzle | 14" PN16 FF (350mm) |  | Discharge Nozzle | 12" PN16 FF (300mm)
Min Straight Length | 5D suction, no reducer/elbows |  | Noise Limit | 85 dBA combined
PACKAGE WEIGHTS
Item | Weight (kg)
Pump (bare) | 1160
Rotor Assembly | 173
Top Casing | 272
Motor (CGL NG450) | 5300
Baseplate (IS2062) | 3250
Coupling (Rathi Spacer Tyre) | 50
Accessories | 50
Acoustic Enclosure (ARK) | 2350
TOTAL PACKAGE | 12160
MOTOR DATA (CGL)
Make | Crompton Greaves Ltd (CGL), Bhopal
Work Order No. | 2241805
Rating | 550 kW
Voltage | 690 V / 3 Phase / 50 Hz
Poles | 4 Pole
Frame Size | NG450
Cooling | IC411
Speed Range | 1143 to 1233 rpm (VFD driven)
Drive Method | VFD (VVVFD)
Locked Rotor Current | 600% FLC at 100% V
Starting Time @100%V | 3 sec
Starting Time @80%V | 4 sec
Starting Time @110%V | 2 sec
Efficiency @60% load | ~94%
Efficiency @80% load | ~95%
Efficiency @100% load | ~95.5%
Power Factor @100% load | ~0.87
Thermal Withstand (Hot) | 20 sec at 100% RV
Thermal Withstand (Cold) | 25 sec at 100% RV
Derating Applied | 10% for 50°C ambient + 900m altitude
Negative Sequence | (I2/In)² × t = 15 (continuous withstand)
DOL Curves Applicability | DOL curves NOT applicable — VFD start
MECHANICAL SEAL & COUPLING
Seal Make | Flowserve Sanmar
Seal Plan | Plan 11 + Plan 62
Plan 62 Flush | Water: 0.5 to 1.0 LPM ¦ Pressure: 1 kg/cm²
Plan 11 Piping MOC | A106 Gr B (CS pipe), A312 Gr 316L (SS pipe/nipple), A182 F316L (SS flange), A240 Gr 316L (orifice plate)
Coupling Make | Rathi Couplings
Coupling Type | Spacer Tyre
DBSE | 250 mm
Coupling Weight | 50 kg
Coupling Guard | Non-sparking Aluminum (Flowserve scope)
NOZZLE CONNECTION DETAILS
Mark | Description | Size | Class | Flange Type | Qty/Pump | Notes
Ns | Suction Flange | 14" | PN 16 | Flat Face (FF) | 1 | Counter flange A105, loose by Flowserve
Nd | Discharge Flange | 12" | PN 16 | Flat Face (FF) | 1 | Counter flange A105, loose by Flowserve
C | Casing Drain | 1/2" | NPT | Plugged | 2 | Never connect to common header without isolation valve
V | Casing Vent | 1/2" | NPT | Plugged | 3
L1 | Baseplate Drain | 2" | NPT | — | 1
M1 | Bearing Housing Oil Fill/Vent | 3/8" | NPT | Plugged | 2 | Thrust bearing flooded oil lubricated
M2 | Bearing Housing Oil Drain | 3/4" | NPT | Plugged | 2
N1 | Casing Plan 11 Connection | 1/2" | 150# | SWRF | 2
N2 | Seal Plan 11 Connection | 1/2" | 150# | SWRF | 2
N3 | Seal Plan 62 Connection | 1/2" | NPT | Plugged | 2 | Water flush 0.5-1.0 LPM @ 1 kg/cm²
N4 | Seal Drain Connection | 1/2" | NPT | Plugged | 2
FOUNDATION & STRUCTURAL
Foundation Bolts | 14 Nos. Ø3/4" (Ø25mm holes), Mild Steel HDG, 14 Nos. M20 jacking bolts
Baseplate Length | 4800 mm
Grout | Shrinkkomp-30 or Fosroc Conbextra-GP2 (non-shrink high strength)
Earthing | 2 Nos. earthing boss (M10 Brass) on diagonally opposite sides of baseplate
CoG Pump | X=600mm, Y=0, Z=1055mm from baseplate CL origin
CoG Motor | X=2750mm, Y=0, Z=1127mm
CoG Total | X=2382.6mm, Y=0, Z=869.5mm
Static Load (max bolt) | 2093 kg (bolts 7 & 8 under motor)
Dynamic Load (motor bolts) | ±291 kg (bolts 7,8,9,10)
Nozzle Load Suction Fx/Fy/Fz | 7120N / 8900N / 5790N
Nozzle Moment Mx/My/Mz (Suction) | 6370Nm / 3120Nm / 4750Nm

## Wilo_GSN_Taljhari_Summary
DISSECTION SUMMARY — WILO 150-200-GSN 2-STAGE PUMP (TALJHARI)
Project: Taljhari & Borio RWS Scheme, DW&S Sahibganj ¦ Doc: Wilo SO 81343152/11 ¦ Customer: Sudhakara Infratech ¦ End Customer: DW&S Div Sahibganj
PUMP IDENTITY
Pump Model | Wilo 150-200-GSN (2-Stage)
Manufacturer | Wilo Mather & Platt Pumps Pvt Ltd, Pune-19
Service | Clear Water Supply to ESR (Taljhari)
Wilo Sales Order No. | 81343152/11
Quantity | 2 Nos.
Type | Horizontal Split Casing (HSC), 2-Stage, Single Volute, Foot Mount
Standard | IS 6595
Drawing / Curve Ref | GSN150-MC/12-P4-0-1480
Rotation | CCW from impeller end (driving end = CW from DE)
Fluid | Clear Water ¦ SG=1 ¦ Viscosity=1 cps ¦ pH=7 ¦ Temp=30°C
Application | Rural Water Supply — Drinking Water & Sanitation
PUMP PERFORMANCE (DUTY POINT)
Parameter | Value |  | Parameter | Value
Flow (Q) | 5060 LPM / 303.6 m³/h |  | Head (H) | 150.0 m
Speed | 1489 RPM |  | Efficiency | 75.77%
Shaft Input Power | 163.68 kW |  | Motor Rating | 200 kW
No. of Stages | 2 |  | NPSHR | 4.57 m (MWC)
Shutoff Head | 171 m |  | Min Continuous Flow | 1750 LPM
Suction Nozzle | 200 mm (Flange ANSI 125/150 FF) |  | Discharge Nozzle | 150 mm (Flange ANSI 125/150 FF)
Max Head (Rated Imp) | 171 m |  | Total Static Load | 2175 kg
MATERIAL OF CONSTRUCTION
Component | Material | Spec / Standard | Notes
Casing (Top & Bottom Half) | Cast Iron | IS 210 Gr FG 260 | Axial (horizontal) split; single volute
Impeller 1st Stage (RH) | Bronze LTB5 | IS 318 Gr LTB5 | Closed type; shaft mounted
Impeller 2nd Stage (LH) | Bronze LTB5 + Coating | IS 318 Gr LTB5 | 2-stage; coated for water service
Shaft | Stainless Steel 410 | ASTM A276 Gr 410 | Solid shaft; Ø90mm at coupling; SS410
Shaft Sleeve | SS410 | ASTM A276 Gr 410 | Under gland packing; 2 nos
Neck Ring / Casing Wear Ring | Bronze LTB5 | IS 318 Gr LTB5 | 2 nos; wear protection
Gland Packing | Graphited Cotton | Manufacturer Std | Standard stuffing box sealing
Stuffing Box / Gland | Cast Iron | IS 210 Gr FG 260 | Stuffing box cover, gland CI
Lantern Ring | Glass Filled Nylon (GFN) | Manufacturer Std | In stuffing box assembly
Bearing Housing | Cast Iron | IS 210 Gr FG 260 | Deep groove ball bearings 6311 ZZ; grease lube
Inter-Stage Collar | Cast Iron | IS 210 Gr FG 260 | Between stages
Inter-Stage Ring | Cast Iron | IS 210 Gr FG 260 | Stage separation
O-Ring | Nitrile Rubber (NBR) | Manufacturer Std | Casing sealing
WEIGHTS
Item | Weight (kg) | Notes
Complete Pump Package (Static Load) | 2175 | From GA drawing; total static load per Wilo datasheet
Motor (Kirloskar SA315M 200kW) | 1350 | From motor datasheet
Pump (bare — estimated) | ~825 | Total 2175 - Motor 1350 = ~825 kg estimated
MOTOR DATA (KIRLOSKAR ELECTRIC — KECL)
Make | Kirloskar Electric Company Ltd (KECL), Unit-II Hubli
Frame | SA315M
Output | 200 kW
Voltage / Frequency | 415V ±10% / 3Ph / 50Hz ±5%
Poles / Sync Speed | 4 Pole / 1500 RPM
Full Load Speed | 1484 RPM
Full Load Current | 332 A
Starting Method | Star-Delta (Y-Δ)
Cooling | IC01 (Open Drip Proof)
Protection | IP23
Insulation Class | F (Temp rise limited to Class B)
Duty | S1 Continuous
Efficiency — Full/3/4/1/2 Load | 94% / 92.5% / 88%
Power Factor — Full/3/4/1/2 Load | 0.90 / 0.89 / 0.84
LRC (DOL / Y-Δ) | 6x / 2x FLC
LRT (DOL / Y-Δ) | 1.9x / 0.57x
Pull-Out Torque (POT) | 2.5x
Stall Time Cold/Hot (DOL) | 30s/15s; at Y-Δ: 89s/44s
Motor GD² | 30 kgm²
Motor Weight (approx) | 1350 kg
DE Bearing | 6319 C3
NDE Bearing | 6315 C3
Terminal Box Position | As per GAD
Connection | Delta (6 terminals)
Accessories | ACH (2x65W/240V) + RTD Simplex Type 6 nos
Paint | RAL 5010
Cable | 2R x 3C x 240 sq.mm
GAD Reference No. | 32210424
Thermal Withstand HOT (100%V) | 107 sec (datasheet curve)
Thermal Withstand COLD (100%V) | 60 sec
EXPANDED PARTS LIST (from Wilo Cross Section 81343152-20 CS)
Item No. | Description | Qty | Material | Notes
1001 | Casing Top Half | 1 | CI IS 210 FG 260
1002 | Casing Bottom Half | 1 | CI IS 210 FG 260 + Coating
1090 | Intermediate Bearing Bush | 1 |  | Between stages
1100 | Inter-Stage Collar | 1 | CI IS 210 FG 260
1181 | Neck Ring (Wear Ring) | 2 | Bronze LTB5
1503 | Impeller 1st Stage (RH) | 1 | Bronze LTB2 + Coating | Item on cross section
1504 | Impeller 2nd Stage (LH) | 1 | Bronze LTB5 + Coating
1750 | Inter-Stage Ring | 1 | CI IS 210 FG 260
1800 | Shaft | 1 | SS410 ASTM A276 Gr 410 | Solid; Ø90mm at coupling
2070 | Water Deflector | 2 | Nitrile Rubber
2100 | Shaft Sleeve | 2 | SS410 | Under packing
2111 | Spacer Sleeve | 2 | SS410
2300 | Lantern Ring | 1 | GFN (Glass Filled Nylon)
2310 | Gland | 2 | CI IS 210 FG 260
2404 | Stuffing Box Cover | 2 | CI IS 210 FG 260
2410 | Gland Packing | — | Graphited Cotton | Standard gland packing
2600 | Deep Groove Ball Bearing | 2 | Steel 6311 ZZ | Grease lubricated
2753 | Bearing End Cover DE (Outer) | 1 | CI
2756 | Bearing End Cover NDE (Outer) | 1 | CI
2760 | Bearing Housing | 2 | CI IS 210 FG 260
3010 | Lock Nut | 1 | Steel KM11
3020 | Locking Washer | 1 | Steel MB11
3031 | Sleeve Nut (LH) | 2 | SS410
3032 | Sleeve Nut (RH) | 2 | SS410
3200 | Impeller Key | 1 | SS410
3250 | Coupling Key | 1 | SS410
4250 | O-Ring | 7 | Nitrile Rubber | Casing sealing

## Wilo_GSN_Borio_Summary
DISSECTION SUMMARY — WILO 150-200-GSN 2-STAGE PUMP (BORIO)
Project: Taljhari & Borio RWS Scheme, DW&S Sahibganj ¦ Doc: Wilo SO 81343152/20 ¦ Customer: Sudhakara Infratech ¦ End Customer: DW&S Div Sahibganj
PUMP IDENTITY
Pump Model | Wilo 150-200-GSN (2-Stage) — Borio ESR
Manufacturer | Wilo Mather & Platt Pumps Pvt Ltd, Pune-19
Service | Clear Water Supply to ESR (Borio)
Wilo Sales Order No. | 81343152/20
Quantity | 2 Nos.
Type | Horizontal Split Casing (HSC), 2-Stage, Single Volute, Foot Mount
Standard | IS 6595
Drawing / Curve Ref | GSN150-MC/12-P4-0-1480 (same series as Taljhari)
Rotation | CCW from impeller end
Fluid | Clear Water ¦ SG=1 ¦ Temp=30°C
Note | Same pump model as Taljhari but different duty point and lower total weight
PUMP PERFORMANCE (DUTY POINT)
Parameter | Value |  | Parameter | Value
Flow (Q) | 5170 LPM / 310.2 m³/h |  | Head (H) | 143.83 m
Speed | 1488 RPM |  | Efficiency | 76.10%
Shaft Input Power | 159.66 kW |  | Motor Rating | 190 kW (Non-Standard)
No. of Stages | 2 |  | NPSHR | Flooded (not specified)
Max Head (Rated Imp) | 166 m |  | Min Continuous Flow | 1750 LPM
Suction Nozzle | 200 mm ANSI 125/150 FF |  | Discharge Nozzle | 150 mm ANSI 125/150 FF
Max Impeller Power | 175.59 kW |  | Total Static Load | 1823 kg
MATERIAL OF CONSTRUCTION
Component | Material | Spec / Standard | Notes
Casing (Top & Bottom Half) | Cast Iron | IS 210 Gr FG 260 | Axial (horizontal) split; single volute
Impeller 1st Stage (RH) | Bronze LTB5 | IS 318 Gr LTB5 | Closed type; shaft mounted
Impeller 2nd Stage (LH) | Bronze LTB5 + Coating | IS 318 Gr LTB5 | 2-stage; coated for water service
Shaft | Stainless Steel 410 | ASTM A276 Gr 410 | Solid shaft; Ø90mm at coupling; SS410
Shaft Sleeve | SS410 | ASTM A276 Gr 410 | Under gland packing; 2 nos
Neck Ring / Casing Wear Ring | Bronze LTB5 | IS 318 Gr LTB5 | 2 nos; wear protection
Gland Packing | Graphited Cotton | Manufacturer Std | Standard stuffing box sealing
Stuffing Box / Gland | Cast Iron | IS 210 Gr FG 260 | Stuffing box cover, gland CI
Lantern Ring | Glass Filled Nylon (GFN) | Manufacturer Std | In stuffing box assembly
Bearing Housing | Cast Iron | IS 210 Gr FG 260 | Deep groove ball bearings 6311 ZZ; grease lube
Inter-Stage Collar | Cast Iron | IS 210 Gr FG 260 | Between stages
Inter-Stage Ring | Cast Iron | IS 210 Gr FG 260 | Stage separation
O-Ring | Nitrile Rubber (NBR) | Manufacturer Std | Casing sealing
WEIGHTS
Item | Weight (kg) | Notes
Complete Pump Package (Static Load) | 1823 | From GA drawing; total static load per Wilo datasheet
Motor (Non-Standard 190kW) | ~1250 | Approx per datasheet; non-standard motor rating
Pump (bare — estimated) | ~573 | Total 1823 - Motor 1250 = ~573 kg estimated
MOTOR DATA
Make | Kirloskar Electric Company Ltd (KECL)
Rating | 190 kW — NON-STANDARD RATING (flagged in Wilo datasheet)
Voltage | 415V / 3Ph / 50Hz
Poles / Speed | 4 Pole / 1488 RPM (Full Load)
Full Load Current | ~309 A (estimated proportional to 200kW/332A)
Starting Method | Star-Delta (Y-Δ)
Weight (approx) | 1250 kg
Note | 190kW is non-standard — Wilo datasheet flags this explicitly. Verify with KECL
NOTES — DIFFERENCE FROM TALJHARI PUMP
Key Difference 1 | Lower duty point: Q=5170 LPM (vs 5060) at H=143.83m (vs 150m)
Key Difference 2 | Lower motor rating: 190kW non-standard (vs 200kW standard for Taljhari)
Key Difference 3 | Lower total package weight: 1823 kg (vs 2175 kg for Taljhari)
Key Difference 4 | Wilo SO number different: 81343152/20 (vs 81343152/11 for Taljhari)
Similarity | Same pump model, same frame, same MOC, same bearing arrangement

## Jyoti_400TE3D4_Summary
DISSECTION SUMMARY — JYOTI 400TE3D4 (5-STAGE VERTICAL TURBINE PUMP)
Project: MP Jal Nigam Pawai ¦ Customer: Zetwerk Manufacturing ¦ Report: SP-PT25-P31722_3 Rev R0 ¦ Date: 30-06-2025 ¦ Drawing: GA/CS-2022
PUMP IDENTITY
Pump Model | Jyoti 400TE3D4
Manufacturer | Jyoti Ltd, Vadodara, Gujarat
Report No. | SP-PT25-P31722_3
Sale Note No. | P31722_3
Service | Water Supply — MP Jal Nigam Pawai Project
Customer | Zetwerk Manufacturing Businesses Pvt Ltd
Quantity | 2 Nos.
Pump Type | Vertical Turbine Pump (VTP)
No. of Stages | 5
Discharge Type | Above Floor
Column Assembly Size | 300 x 60 mm (Column Pipe Ø300mm NB / Line Shaft Ø60mm NB)
Discharge Assembly Size | DS-300
Lubrication | Self Water (water-lubricated line shaft bearings)
Fluid | Water ¦ SG=1
Sealing Type | Gland Packing (Standard)
PUMP PERFORMANCE (DUTY POINT)
Parameter | Bowl Value | Pump Value | Units | Notes
Capacity | 10234 | 10234 | LPM (614 m³/h) | Duty point
Head | 116 | 115.537 | m | Bowl head / Pump head
Efficiency | 84.00% | 83.00% | % | Bowl / Pump efficiency
Input Power | 230.93 | 231.68 | kW | Bowl / Pump input power
Speed | 1480 | 1480 | RPM | Motor speed
Shutoff Head | 154.29 | — | m | 133% of bowl head
Specific Speed | 2990.54 | — | US Units
Impeller Dia Rated | ø326* | — | mm | *Subject to final Jyoti performance data
Impeller Dia Max | ø327 | — | mm
Impeller Dia Min | ø308 | — | mm
GD² (Pump) | 4.25 | — | kgm²
Vibration Limit | 4.5 | — | mm/s max
Noise Limit | 85 | — | dB @ 1.85m
Pump Weight | 5280 | — | kg | Pump only
Motor Weight | 2800 | — | kg | Motor only
MATERIAL OF CONSTRUCTION
Component | Material | Standard / Spec | Item No.
Bowl (Stage Casing) x5 | SG Iron (Spheroidal Graphite Iron) | IS 1865 | Item 6
Top Bowl | SG Iron | IS 1865 | Item 8
Impeller (Closed) x5 | SS CF8M Stainless Steel | ASTM A743 | Item 5
Impeller Wearing Ring x5 | Bronze LTB2 | IS 318 Gr LTB2 | Item 4
Impeller Shaft | SS 410T | ASTM A276 | Item 9
Line Shaft | SS 410T | ASTM A276 | Item 2
Head Shaft | SS 410T | ASTM A276 | Item 1"
Line Shaft Coupling | SS 410T | ASTM A276 | Item 7"
Head Shaft Coupling | SS 410T | ASTM A276 | Item 5"
Impeller Shaft Coupling | SS 410T | ASTM A276 | Item 11
Column Pipe (Ø300mm NB) | ERW Steel Pipe | IS 1239 / IS 3589 | Item 1"
Top Column Pipe | CI FG 200 | IS 210 | Item 6"
Discharge Head Body | CI FG 200 | IS 210 | Item 2"
Column Pipe Adaptor (CPA) | CI FG 200 | IS 210 | Item 10
Bearing Holder | CI FG 200 | IS 210 | Item 3"
Line Shaft Bearing | Thordon Type (Water Lube) | Thordon Proprietary | Item 4"
Bush Bearing (Bowl) | Bronze LTB2 | IS 318 Gr LTB2 | Item 7
Suction Case Bearing | Bronze LTB2 | IS 318 Gr LTB2 | Item 3
Suction Case | CI FG 200 | IS 210 | Item 2
Strainer | MS Fabricated | IS 2062 | Item 1
Stuffing Box | CI FG 200 | IS 210 | Item 5"
Gland | CI FG 200 | IS 210 | Item 3"
Gland Packing (Sealing) | Standard Gland Packing | Manufacturer Std | Item 4"
Soleplate | MS Fabricated | IS 2062 | Item *
Motor Skirt | MS Fabricated | IS 2062 | Item 7"
Motor Coupling | CI FG 200 | IS 210 | Item 9"
Pump Coupling | CI FG 200 | IS 210 | Item 8"
Fasteners | Standard | STD | —
WEIGHTS
Item | Weight (kg) | Notes
Pump (complete VTP assembly) | 5280 | From pump datasheet
Motor (Jyoti-supplied CUD315) | 2800 | From pump datasheet
TOTAL PACKAGE | 8080 | Pump 5280 + Motor 2800
Column Length | 19200 mm | 1500x12 + 1200x1; pump floor level 21.953m
Foundation Bolts | 4 Nos AM24 x 500mm | NOT in Jyoti scope of supply
MOTOR DATA (JYOTI-SUPPLIED)
Motor Frame | CUD315
Motor Type | Solid Shaft
Rating | 315 kW / 425 hp
Poles / Speed | 4 Pole / 1480 RPM
Motor Weight | 2800 kg
Foundation Bolt | 4 Nos AM24 x 500mm (not in Jyoti scope)
Static Load at Foundation | 79.26 kN
Dynamic Load Horizontal @Duty | 13.05 kN
Dynamic Load Horizontal @Shutoff | 17.35 kN
Dynamic Load Vertical @Duty | 105.83 kN
Dynamic Load Vertical @Shutoff | 116.83 kN
Force at Discharge Nozzle Fx/Fy/Fz | 76.34 kN / 152.68 kN / 76.34 kN
Moment at Discharge Nozzle Mx/My/Mz | 22.9 kN.m / 48.86 kN.m / 22.9 kN.m
SUMP / INSTALLATION DETAILS
Sump Floor Level | 0 m (datum)
Min Water Level | 2.593 m above sump floor
Min Submergence Level | 2.093 m above sump floor
Pump Floor Level | 21.953 m
Side Wall Clearance | 385 mm
Back Wall Clearance | 288.75 mm
Bowl Diameter | ø396 mm (submerged bowl)
Discharge Flange OD / ID / PCD | ø457 / ø300 / ø406.4 mm; 12 Holes M20; Sq. 500mm port opening

## Jyoti_350TE1A4_Summary
DISSECTION SUMMARY — JYOTI 350TE1A4 (7-STAGE VERTICAL TURBINE PUMP)
Project: MP Jal Nigam Pawai ¦ Customer: Zetwerk Manufacturing ¦ Report: SP-PT25-P31722/1 Rev R0 ¦ Date: 30-06-2025 ¦ Drawing: GA/CS-2021
PUMP IDENTITY
Pump Model | Jyoti 350TE1A4
Manufacturer | Jyoti Ltd, Vadodara, Gujarat
Report No. | SP-PT25-P31722/1
Sale Note No. | P31722/1
Service | Water Supply — MP Jal Nigam Pawai Project
Customer | Zetwerk Manufacturing Businesses Pvt Ltd
Quantity | 2 Nos.
Pump Type | Vertical Turbine Pump (VTP)
No. of Stages | 7
Discharge Type | Above Floor
Column Assembly Size | 200 x 50 mm (Column Pipe Ø200mm NB / Line Shaft Ø50mm NB)
Discharge Assembly Size | DS-200
Lubrication | Self Water (water-lubricated line shaft bearings)
Fluid | Water ¦ SG=1
Sealing Type | Gland Packing (Standard)
Comparison | Same project as 400TE3D4 but smaller duty — half the flow
PUMP PERFORMANCE (DUTY POINT)
Parameter | Bowl Value | Pump Value | Units | Notes
Capacity | 5117 | 5117 | LPM (307 m³/h) | Duty point
Head | 116 | 115.049 | m | Bowl head / Pump head
Efficiency | 81.00% | 80.00% | % | Bowl / Pump efficiency
Input Power | 119.74 | 120.49 | kW | Bowl / Pump input power
Speed | 1480 | 1480 | RPM | Motor speed
Shutoff Head | 177.8 | — | m | 153% of bowl head
Specific Speed | 2713.69 | — | US Units
Impeller Dia Rated | ø279.9* | — | mm | *Subject to final Jyoti performance data
Impeller Dia Max | ø286 | — | mm
Impeller Dia Min | ø256 | — | mm
GD² (Pump) | 1.015 | — | kgm²
Vibration Limit | 4.5 | — | mm/s max
Noise Limit | 85 | — | dB @ 1.85m
Pump Weight | 3350 | — | kg | Pump only
Motor Weight | 1350 | — | kg | Motor only
MATERIAL OF CONSTRUCTION
Component | Material | Standard / Spec | Item No.
Bowl (Stage Casing) x7 | SG Iron | IS 1865 | Item 6
Top Bowl | SG Iron | IS 1865 | Item 8
Impeller (Closed) x7 | SS CF8M | ASTM A743 | Item 5
Impeller Wearing Ring x7 | Bronze LTB2 | IS 318 Gr LTB2 | Item 4
Impeller Shaft | SS 410T | ASTM A276 | Item 9
Line Shaft (Ø50mm NB) | SS 410T | ASTM A276 | Item 2"
Head Shaft | SS 410T | ASTM A276 | Item 1"
Line Shaft Coupling | SS 410T | ASTM A276 | Item 7"
Column Pipe (Ø200mm NB) | ERW Steel Pipe | IS 1239 / IS 3589 | Item 1"
Top Column Pipe | CI FG 200 | IS 210 | Item 6"
Discharge Head Body | CI FG 200 | IS 210 | Item 2"
Column Pipe Adaptor (CPA) | CI FG 200 | IS 210 | Item 10
Bearing Holder | CI FG 200 | IS 210 | Item 3"
Line Shaft Bearing | Thordon Type | Thordon Proprietary | Item 4"
Bush Bearing (Bowl) | Bronze LTB2 | IS 318 Gr LTB2 | Item 7
Suction Case Bearing | Bronze LTB2 | IS 318 Gr LTB2 | Item 3
Suction Case | CI FG 200 | IS 210 | Item 2
Strainer | MS Fabricated | IS 2062 | Item 1
Stuffing Box + Gland | CI FG 200 | IS 210 | Items 5", 3"
Gland Packing | Standard Gland Packing | Manufacturer Std | Item 4"
Soleplate + Motor Skirt | MS Fabricated | IS 2062 | Items *, 7"
Motor Coupling + Pump Coupling | CI FG 200 | IS 210 | Items 9", 8"
Fasteners | Standard | STD | —
WEIGHTS
Item | Weight (kg) | Notes
Pump (complete VTP assembly) | 3350 | From pump datasheet
Motor (Jyoti-supplied CUTF315) | 1350 | From pump datasheet
TOTAL PACKAGE | 4700 | Pump 3350 + Motor 1350
Column Length | 19100 mm | 1500x12 + 1100x1; pump floor level 22.039m
Foundation Bolts | 4 Nos AM24 x 500mm | NOT in Jyoti scope of supply
MOTOR DATA (JYOTI-SUPPLIED)
Motor Frame | CUTF315 (IE-III)
Motor Type | Solid Shaft
Rating | 160 kW / 215 hp
Poles / Speed | 4 Pole / 1480 RPM
Motor Weight | 1350 kg
Foundation Bolt | 4 Nos AM24 x 500mm (not in Jyoti scope)
Static Load at Foundation | 46.11 kN
Dynamic Load Horizontal @Duty | 9.98 kN
Dynamic Load Horizontal @Shutoff | 15.3 kN
Dynamic Load Vertical @Duty | 88.26 kN
Dynamic Load Vertical @Shutoff | 101.03 kN
Force at Discharge Nozzle Fx/Fy/Fz | 30.79 kN / 61.58 kN / 30.79 kN
Moment at Discharge Nozzle Mx/My/Mz | 6.16 kN.m / 14.47 kN.m / 6.16 kN.m
SUMP / INSTALLATION DETAILS
Sump Floor Level | 0 m (datum)
Min Water Level | 1.982 m above sump floor
Min Submergence Level | 1.482 m above sump floor
Pump Floor Level | 22.039 m
Side Wall Clearance | 340 mm
Back Wall Clearance | 255 mm
Bowl Diameter | ø350 mm (submerged bowl)
Discharge Flange OD / ID / PCD | ø343 / ø200 / ø292 mm; 8 Holes M16; Sq. 410mm port opening
COMPARISON — 400TE3D4 vs 350TE1A4 (Same Project)
Parameter | 400TE3D4 (Larger) | 350TE1A4 (Smaller) | Ratio
Flow | 10234 LPM | 5117 LPM | 2:1
Stages | 5 | 7 | —
Bowl Head | 116m | 116m | Same
Pump Efficiency | 83% | 80% | —
Motor Rating | 315 kW | 160 kW | ~2:1
Pump Weight | 5280 kg | 3350 kg | 1.57:1
Column Size | 300 x 60mm | 200 x 50mm | —
Discharge | DS-300 | DS-200 | —
Impeller Dia Rated | ø326mm | ø279.9mm | —
Bowl Dia | ø396mm | ø350mm | —
GD² Pump | 4.25 kgm² | 1.015 kgm² | 4.2:1

## Wilo_MPS3_Summary
DISSECTION SUMMARY — WILO MPS-3 1-STAGE VERTICAL TURBINE PUMP
Project: Sauni Yojana Link-2 Package-9 ¦ FPS-8 Shell Dedumal ¦ Approval: Bhavnagar Irrigation Project Div (Approval 9-35, 11/09/2023) ¦ GAD: 81332087-10 Rev 03
PUMP IDENTITY
Pump Model | Wilo MPS-3 (1-Stage VTP)
Manufacturer | Wilo Mather & Platt Pumps Pvt Ltd, Pune-19
Drawing No. | 81332087-10 GA Rev 03
Wilo SO No. | 81332087
Service | Water Supply — Sauni Yojana Link-2 Package-9, FPS-8 Shell Dedumal
Client / Owner | Bhavnagar Irrigation Project Division (G2 WRD)
LSTK Contractor | Zetwerk Manufacturing Businesses Pvt Ltd
TPI (Inspection) | Technomen Consultants, Gandhinagar
Approval Ref | Approval 9-35 dated 11/09/2023; No. PB-3/Sauni-L2P9/Hindustan Project/Approval/HT & LT MOTOR / 21ℒ66
Pump Type | Vertical Turbine Pump (VTP), 1-Stage
Bore | 450 mm NB (Delivery pipe bore)
Lubrication | Antifriction Oil Lubricated
Direction of Rotation | CW from top (antifriction oil)
Motor Frame | VPC710 (CGL make)
Motor Rating | 260 kW
PUMP PERFORMANCE (FROM GAD 81332087-10)
Parameter | Value | Units | Notes
Flow (Q) | 68 | m³/h | From GAD nameplate block
Head (H) | 68 | m | From GAD nameplate block
Speed | 1482 | RPM | Full speed
Motor Rating | 260 | kW | CGL VPC710 frame
Bowl Efficiency | 58.28% | % | From GAD data block
No. of Stages | 1 | — | Single stage MPS-3
No. of Pumps | — | — | Part of FPS-8 Shell Dedumal feeder station
STRUCTURAL / INSTALLATION DETAILS (FROM GAD)
Parameter | Value | Notes
Total Assembly Height | 6500 mm (approx) | Overall from sump to motor top
Min Submergence (Min. Reqd.) | 2185 mm | From GAD
Column Length | 4600 mm | 1200x3 + 1000x1 per revision note
Delivery Pipe Length | 1500 + 1990 mm | Upper delivery section
Base Frame | 2100 CTC x 2200 SQ mm | Plan view of base frame at Z-Z
Foundation Bolt Holes | 16 Nos M30 Drill | For pump mounting
Grouting | Required per standard | Base frame grouted
Motor Stool | — | Connects motor to pump discharge head
Coupling End (Pump Shaft) | Ø45 mm bore | Per coupling end detail drawing
Coupling End (Motor Shaft) | Ø100 mm bore | Per coupling end detail drawing
Base Frame Plate Thickness | 8mm revised to 14mm | Per revision note on GAD Rev 03
Hook Height (Min) | 5500 mm | For erection / lifting
MOTOR DATA (CGL VPC710)
Make | CGL (Crompton Greaves Ltd)
Frame | VPC710
Rating | 260 kW
Speed | 1482 RPM (full speed)
Lubrication | Antifriction Oil (motor bearings)
Mounting | Vertical hollow/solid shaft for VTP
Approval Status | Approved by Bhavnagar Irrigation Project Division (Approval 9-35)
Document Ref | HT Induction Motor approved — see Approval letter No. PB-3/Sauni-L2P9 dated 11/09/2023
Note | Motor datasheet and QAP also approved as part of same package (HT & LT Motors, Jyoti Ltd Vadodara)
PROJECT / APPROVAL CONTEXT

## ksb stgc 050
DISSECTION SUMMARY — KSB STGC 050-160-CC-WDL DILUTE ACID SUMP PUMP
Project: NALCO 1.0 MTPA Alumina Refinery Stream-5 ¦ KSB S.O. 9975641078/0100 ¦ Client PO: ZET-OD-KSB2-2 dt.09.12.2024 ¦ Drawing: F9975641078-1 R5
PUMP IDENTITY
Pump Model | KSB STGC 050-160-CC-WDL
Manufacturer | KSB Limited (India)
KSB S.O. No. | 9975641078/0100
Client P.O. No. | ZET-OD-KSB2-2 dt.09.12.2024
Customer Item No. | 08PU-J5893 — Acid Area Sump Pump
Quantity | 1 No.
Service | Dilute Sulphuric Acid Sump Pump
Location | Evaporation Unit, NALCO Damanjodi, Odisha
Type | Vertical Sump Pump — KSB STGC series
Direction of Rotation | Clockwise from DE
ZW Drawing No. | ZT2023.02-508-GA-ME-241
Drawing Rev | R5 (27-Nov-2025)
Technology Partner | Metso Outotec (Germany) / Outotec India Pvt Ltd
LSTK Contractor | Zetwerk Manufacturing Businesses Pvt Ltd
Consultant | Triple I Engineers, Hyderabad
PUMP PERFORMANCE (DUTY POINT)
Parameter | Value | Units | Notes
Rated Flow | 80 | m³/h | From pump duty block on drawing
Rated Head | 30 | m | From pump duty block on drawing
Speed | 2940 | RPM | Motor speed (2-pole)
Motor Rating | 15 | kW | ABB 160M frame
GD² of Pump | 0.0434 | kgm² | From drawing data block
Dynamic Load per Fixing Bolt | 3162 | kgf | From drawing data block
Fluid | Dilute Sulphuric Acid | — | Corrosive service
Installation Depth | 1973 | mm | From FFL to tank bottom
Tank Thickness | 10 | mm | Acid tank wall
Min Liquid Level | 240 | mm | From drawing
FFL (Floor Level) | EL +930.300m | —
Tank Bottom | EL +928.290m | —
HL to LL Height | 700 | mm | From drawing
MOTOR DATA (ABB)
Make | ABB
Frame | 160M
Rating | 15 kW
Speed | 2940 RPM
Enclosure | TEFC — IE3
Weight | 126 kg
Direction | Clockwise from DE
Pump Shaft End Bore | Ø24 mm
Motor Shaft End Bore | Ø45 mm
Overall Height (with motor) | 2023 mm
Overall Height (without motor) | 1033 mm
Fixation Holes | Ø20 mm
Fixing Bolts | 4 Nos M16 x 200 LG; Ø20 holes on mounting plate
FLANGE DETAILS — DISCHARGE DN65
Parameter | Value | Standard
Nozzle Size | DN65 | ASME B16.5
Outer Diameter | 178 mm
PCD | 139.7 mm
BCD | 184.7 mm
No. of Holes | 4
Hole Size | Ø19 mm
Force Fy | 893 N | Allowable nozzle load
Force Fz | 1103 N
Force Fx | 971 N
Moment My | 420 Nm
Moment Mz | 490 Nm
Moment Mx | 700 Nm
WEIGHTS
Item | Weight (kg) | Notes
Pump (Empty) | 193 | From drawing data block
Pump (Operating — with liquid) | 243 | From drawing data block
Motor (ABB 15kW 160M) | 126 | From drawing data block
TOTAL WEIGHT | 319 | Pump empty 193 + Motor 126
SCOPE OF SUPPLY (KSB)
✓ Pump (STGC 050-160-CC-WDL)
✓ Suction Strainer
✓ Coupling (RB — Rathi make)
✓ Coupling Guard
✓ Motor (ABB 15kW 160M IE3)
✓ Mounting Plate
✓ Gasket & Hardware
✓ 4 Nos Ø20 Fixing Bolts M16x200
✗ NOT in scope: Concrete block / civil foundation; V/S Drive

## ksbvs6
DISSECTION SUMMARY — KSB VS6 PROCESS CONDENSATE PUMP (DS-ME-115)
Project: NALCO 1.0 MTPA Alumina Refinery Stream-5 ¦ Doc: ZT2023.02-508-DS-ME-115 Rev 3 ¦ Tags: 08PU-J5813A/B & 08PU-K5813A/B ¦ LSTK: Zetwerk
PUMP IDENTITY
Pump Model | KSB VS6 (API 610 VS6 or equivalent)
Manufacturer | KSB Limited (India) — VTA (Vendor to Advise)
Tag Numbers | 08PU-J5813A/B & 08PU-K5813A/B
Quantity | 4 Nos. (2 each for Evaporation Unit J & K)
Service | Process Condensate Pump
Location | Evaporation Unit J & K, Damanjodi, Odisha — Outdoor
Elevation | 900 m above sea level
Ambient Pressure (design) | 89 kPa
Ambient Temperature | 3°C min / 50°C max
Type | API 610 VS6 or equivalent — Double-Casing, Diffuser, Inline Suction & Discharge
Configuration | Each Unit: 1 Working + 1 Standby
Operation | Single pump, continuous, variable speed (VSD by purchaser)
Design Standard | Vendor Standard / API 610
Datasheet Doc | ZT2023.02-508-DS-ME-115 Rev 3
Condensate Pot Tag | 08PV-J/K-5813 (discharge nozzle at 0.53m above ground)
Note on NPSH | NPSHA=0.5m — VS6 type specifically required for very low NPSH operation
PUMP PERFORMANCE — THREE OPERATING POINTS
Parameter | OP1 MinFlow | OP2 Normal | OP3 MaxFlow | Rated | Units
Volume Flow | 99 | 141 | 198 | 172 | m³/h
Pump Head | 73.2 | 73.7 | 75.0 | 74.3 | m
Operating Temperature | 47 | 47 | 47 | 47 | °C
Density | 990 | 990 | 990 | 990 | kg/m³
Dynamic Viscosity | 0.6 | 0.6 | 0.6 | 0.6 | mPa.s
Vapour Pressure (abs) | 10 | 10 | 10 | 10 | kPa(a)
Inlet Pressure (gauge) | -74 | -74 | -76 | -74 | kPa(g)
Differential Pressure | 711 | 716 | 728 | — | kPa
NPSHA | — | — | — | 0.5 | m
Speed (nominal) | — | — | — | 1450 | rpm (VSD)
Shaft Power | — | — | — | VTA | kW
Motor Rating | — | — | — | VTA | kW
Efficiency | — | — | — | VTA | %
NPSHR | — | — | — | VTA | m
Min Allowable Flow | — | — | — | VTA | m³/h
MATERIAL OF CONSTRUCTION
Component | Material | Standard/Spec | Notes
Suction Casing | CS ASTM A216 Gr WCB | ASTM A216 | Carbon steel casting
Stage Casing | CS ASTM A216 Gr WCB | ASTM A216 | Carbon steel casting
Discharge Casing | CS ASTM A216 Gr WCB | ASTM A216 | Carbon steel casting
Diffuser | VTA | — | Vendor to advise
Impeller | SS 2324 (Lean Duplex) | SS 2324 | Better corrosion resistance than SS304
Impeller Wear Ring | VTA | —
Case Wear Ring | VTA | —
Bearing Housing | VTA | —
Shaft | VTA | —
Shaft Sleeve | VTA | —
Stuffing Box | VTA | —
Casing Bolts | VTA | —
Gland / Seal Plate | VTA | —
Base Frame | Carbon Steel | — | CS as specified
Base Plate | VTA | —
Coupling Halves | VTA | —
CONSTRUCTION FEATURES (VTA = Vendor to Advise)
Volute Casing Type/Split | VTA
No. of Stages | VTA
Type of Impeller | VTA
Impeller Diameter (Min/Max) | VTA
Casing Test Pressure | VTA
Casing Mounting | VTA
Drive Type | Flexible coupling with spacer
Bearings | VTA
Lubrication | VTA
Shaft Seal | Mechanical Seal (seal flushing plan — vendor to advise per Ref #06)
Thrust Balancing | VTA
Flange Standard & Rating | ASME (125-250 AARH surface finish)
Cooling Plan | VTA
Seal Flushing Plan | VTA
Noise Level | ≤ 85 dB(A) at 1m periphery
Vibration Limit | VTA
GD² of Pump + Coupling | VTA
Direction of Rotation | VTA
Painting Spec | 6695-EQS-G00-EC-0007
MOTOR DATA
Motor Type | Squirrel Cage Induction Motor
Nominal Power | VTA
Poles / Nominal Speed | 4 Pole / VTA rpm
Voltage / Frequency | 415V ±10% / 50Hz +3%/-5% / 3-Phase
Ambient Temperature | 50°C
Motor Provided By | Pump Vendor
Drive Method | VSD (Variable Speed Drive — VSD by Purchaser)
Motor Spec Doc | 6695-ELT-G00-EC-0012
SCOPE OF SUPPLY
✓ Pump (VS6 double-casing diffuser)
✓ Motor (squirrel cage)
✓ Common Base Frame (CS)
✓ Coupling & Coupling Guard
✓ Companion Flanges with Gaskets & Fasteners
✓ Foundation Bolts
✓ Suction Strainer (start-up type)
✓ Mechanical Seal
✓ First Fill Lubricants
✗ NOT in scope: Suction & Discharge Valves; VSD (by purchaser)
COMPARISON — LIVE STEAM CONDENSATE (DS-114) vs PROCESS CONDENSATE (DS-115)
Parameter | Live Steam Condensate (DS-114) | Process Condensate (DS-115) | Notes
Tags | 08PU-J/K5821A/B | 08PU-J/K5813A/B
Rated Flow | 44.5 m³/h | 172 m³/h | PC pump ~4x higher flow
Rated Head | 113.2 m | 74.3 m | LSC pump higher head (deeper well)
Temperature | 136°C (rated) / 148°C (max) | 47°C | LSC is high temp — condensate from live steam
Density | 930 kg/m³ | 990 kg/m³ | LSC hotter → lower density
Vapour Pressure | 320 kPa(a) | 10 kPa(a) | LSC near saturation — critical NPSH
Inlet Pressure | 235 kPa(g) positive | −74 kPa(g) negative | PC pump has suction under vacuum
Motor | 30 kW (fixed) | VTA
Impeller MOC | SS304 | SS 2324 (Lean Duplex) | Different corrosion requirements
Casing MOC | SS304 throughout | CS WCB casing / SS2324 impeller | PC uses CS for casing
Total Weight | 1561 kg | VTA
NPSHA | 0.5 m | 0.5 m | Both critically low — VS6 required for both

## ksb wkt 80_9
DISSECTION SUMMARY — KSB WKT 80/9 LIVE STEAM CONDENSATE PUMP
Project: NALCO 1.0 MTPA Alumina Refinery Stream-5 ¦ KSB Order: 9975603447/300 ¦ Client PO: ZET-OD-KSB2-1 DT.19/10/2024 ¦ Drawing: F9975603447-300-1 As Built
PUMP IDENTITY
Pump Model | KSB WKT 80/9
Manufacturer | KSB Limited (India)
KSB Order No. | 9975603447/300/400
Client P.O. No. | ZET-OD-KSB2-1 DT.19/10/2024
Tag Numbers | 08PU-J5821A/B & 08PU-K5821A/B
Quantity | 4 Nos. (2 each for Evaporation Unit J & K)
Service | Live Steam Condensate
Location | Evaporation Unit J & K, Damanjodi, Odisha
Elevation | 900m above sea level
Type | API 610 VS6 — Double-Casing, Diffuser, Inline Suction & Discharge, Vertical Turbine Pump
Configuration | Each Unit: 1 Working + 1 Standby
Direction of Rotation | CCW — seen from coupling end
Sealing Arrangement | Plan 13 + 61
Datasheet Ref | ZT2023.02-508-DS-ME-114 Rev 3
Drawing Ref | F9975603447-300-1 As Built
PUMP PERFORMANCE
Parameter | Min Flow (OP1) | Normal (OP2) | Max Flow (OP3) | Rated | Units
Volume Flow | 24 | 34 | 50 | 44.5 | m³/h
Pump Head | 110.6 | 111.6 | 114.1 | 113.2 | m
Operating Temperature | 136 | 136 | 148 | 136 | °C
Density | 930 | 930 | 920 | 930 | kg/m³
Dynamic Viscosity | 0.2 | 0.2 | 0.185 | 0.2 | mPa.s
Vapour Pressure (abs) | 320 | 320 | 446 | 320 | kPa(a)
Inlet Pressure (gauge) | 235 | 235 | 235 | 235 | kPa(g)
Differential Pressure | 1009 | 1018 | 1041 | — | kPa
NPSHA | — | — | — | 0.5 | m
Speed | — | — | — | 1480 | rpm
Shaft Power (BKW) | — | — | — | 24.26 | kW
Motor Power | — | — | — | 30 | kW
Efficiency | — | — | — | 75% | %
MATERIAL OF CONSTRUCTION
Component | Material | Standard/Spec | Notes
Bowl Shaft | SS304 | AISI 304 | Double-casing diffuser bowl assembly
Bowl | SS304 | AISI 304 | Stage casing
Impeller | SS304 | AISI 304 | Closed type; dia VTA
Suction Bell | SS304 | AISI 304 | Inlet bell
Bowl Adapter | VTA | — | Vendor to advise
Bearing Sleeve (Bowl) | VTA | —
Bowl Wear Ring | VTA | —
O-Ring | VTA | —
Column Pipe | SS304 | AISI 304
Line Shaft | SS304 | AISI 304
Bearing Retainer | VTA | —
Bearing Sleeve (Line Shaft) | VTA | —
Shaft Sleeve | SS316 | AISI 316
Shaft Coupling | SS316 | AISI 316
Column Pipe Fasteners | SS316 | AISI 316
Discharge Head | SS304 | AISI 304
Top Shaft | VTA | —
Seat Chamber / Stuffing Box | VTA | —
Coupling | REM 65-250 B/B | KSB Std | GD²=0.013 kgm²
Counter Flange — Discharge | ASTM A216 WCB | ASME B16.5 | DN100 CL150 RF
Counter Flange — Suction | ASTM A216 WCB | ASME B16.5 | DN150 CL150 RF
Base Frame / Channel | IS MC 200 Mild Steel | IS:2062 | Square base frame channel
WEIGHTS
Item | Weight (kg) | Notes
Motor (ABB 30kW Frame 225M) | 171 | From As-Built drawing
Pump Barrel + Column Pipe | 1390 | From As-Built drawing
Motor Lantern + Base Frame + Coupling | ~170 (incl) | Included in total
TOTAL WEIGHT | 1561 | From As-Built drawing F9975603447-300-1
GD² of Pump | 0.2454 kgm² | From As-Built drawing
GD² of Coupling | 0.013 kgm² | Coupling REM 65-250 B/B
MOTOR DATA (ABB)
Make | ABB
Frame Size | 225 M
Rating | 30 kW
Speed | 1440/1480 RPM
Voltage/Frequency | 415V / 3Ph / 50Hz
Enclosure | TEFC (Totally Enclosed Fan Cooled)
Ambient Temperature | 50°C
Motor Weight | 171 kg
Direction | CCW from coupling end (pump rotation)
NOZZLE & CONNECTION SCHEDULE
Mark | Description | Size | Type/Rating | Notes
N1 | Vent | 3/4" NPT | Adaptor NPT 3/4" — KSB Scope | with pipe union/ermeto fitting NPT; loose supply; pipe union/ermeto fitting suitable for pipe T schedule 40
N2 | Vacuum Gauge Connection | 1/2" NPT | N/A | Not applicable per drawing
N3 | Plan 13 — Recirculation | DN5 | Std connection DN15 with blind flange | Recirculation from mech seal through orifice to pump suction; not applicable for CEP
N8 | Leakage Drain | 1/2" NPT | Plugged | To be connected drain at site
Discharge | Discharge Nozzle | DN100 | CL150 RF | OD 229mm; PCD 190.5mm; Thk 23.9mm; 8 holes Ø19mm
Suction | Suction Nozzle | DN150 | CL150 RF | OD 279mm; PCD 241.3mm; Thk 25.4mm; 8 holes Ø22mm
Draw-In | Draw-In Barrel | — | N3=150/41 | Forces (kgf): Fx=80, Fy=60.5, Fz=35.5; Moments (kgf.m): 17.2 / 4 / 15.7
FOUNDATION LOADS
Dynamic Load per Foundation Bolt | 80 kgf
Static Load per Foundation Bolt | 84.5 kgf
Foundation Bolt Config | M16-8 Nos. tapped holes on base frame; 8-Nos tapped holes on barrel top plate
Floor Level | FFL +930.300m
SCOPE OF SUPPLY (KSB)
✓ Pump (WKT 80/9)
✓ Mechanical Seal (Plan 13+61)
✓ Coupling (REM 65-250 B/B) & Coupling Guard
✓ Motor (ABB 30kW 225M) & Motor Stool
✓ Base Frame (square channel IS MC 200)
✓ Suction & Discharge Counter Flanges with gaskets & fasteners
✗ NOT in scope: Base frame pad concrete block (by civil); Vacuum gauge; V/S Drive

## BOM_Templates
BOM TEMPLATES — MANDATORY & OPTIONAL COMPONENTS BY PUMP TYPE
PURPOSE: When classifier identifies pump type, this sheet returns the BOM template (mandatory + optional components). Template_ID links to Component_Library. M=Mandatory, O=Optional, C=Conditional
A. TEMPLATE REGISTRY — PUMP TYPE TO TEMPLATE MAPPING
Template_ID | Pump_Type | API_Type | Drive | Stages | Flow_Range_m3h | Head_Range_m | Power_Range_kW | Fluid_Category | Source_Pumps | Description
TPL-HSC-01 | Horizontal Split Casing | BB1/BB2 | Direct Coupled | 1 | 50–2000 | 20–200 | 10–600 | Clean Water / Process | FLW-001, WILO-001, WILO-002 | Axial split casing; between-bearing; clean/process fluid
TPL-HSC-02 | Horizontal Split Casing - High Head | BB2 | Direct Coupled | 1–2 | 50–1200 | 80–300 | 50–700 | Clean Water / Condensate | FLW-001 | High head HSC; PN16+ flanges; API 610 BB2
TPL-HSS-01 | Horizontal Slurry Pump | — | V-Belt/Direct | 1 | 100–2000 | 10–120 | 50–600 | Slurry / Abrasive | METSO-001 | High chrome iron; V-belt or direct drive; wear-liner design
TPL-VTP-01 | Vertical Turbine Pump - Water Supply | VS1/VS6 | Solid Shaft Motor | 1–12 | 50–1000 | 30–200 | 5–400 | Clean Water | JYOTI-001, JYOTI-002, WILO-003 | Column pump; line shaft bearings; above-floor discharge
TPL-VTP-02 | Vertical Turbine Pump - Condensate VS6 | VS6 | Solid Shaft Motor | 1–8 | 10–200 | 50–150 | 5–100 | Hot Condensate / Low NPSH | KSB-003, KSB-005 | Double-casing diffuser; inline suction/discharge; SS304/SS316 wetted parts; API Plan 13+61
TPL-VSP-01 | Vertical Sump Pump | VS4/VS6 | Direct Coupled | 1–3 | 10–300 | 5–60 | 1–75 | Corrosive / Acid / Sump | KSB-004 | Cantilevered shaft; submerged in tank/sump; no bearing below liquid; acid-resistant MOC
TPL-VRT-01 | Vertical Submersible (Borewell/Pit) | VS5 | Direct Coupled | 1–20 | 5–200 | 30–400 | 1–200 | Clean Water / Groundwater | KSB-001, KSB-002 | Submerged motor-pump; column pipe; delivery pipe; motor stool
TPL-MSC-01 | Multistage Centrifugal - Boiler Feed | BB3/OH2 | Direct Coupled | 2–8 | 50–500 | 100–600 | 100–2000 | High-temp Water / Condensate | — | High pressure; balance disc; special sealing; multi-stage; placeholder for future data
TPL-PD-01 | Positive Displacement - Reciprocating | — | Direct/Gear | — | 0.5–50 | 100–5000 | 5–500 | Chemicals / High Viscosity | — | Placeholder — no data yet
B. COMPONENT REQUIREMENTS PER TEMPLATE (M=Mandatory, O=Optional, C=Conditional on service)
Template_ID | Component_Category | Component_Subcategory | Req_Type | Typical_MOC | Qty_Logic | Notes_for_BOM_Generator
TPL-HSC-01 | Pump | Complete Assembly | M | Various | 1 per pump | Main pump unit; look up Component_Library by Pump_Model_Compatibility
TPL-HSC-01 | Casing | Upper Casing | M | A216 WCB / CI FG260 | 1 | Horizontally split; material from Material_Compatibility sheet
TPL-HSC-01 | Casing | Lower Casing | M | A216 WCB / CI FG260 | 1 | Lower half
TPL-HSC-01 | Rotor | Rotor Assembly | M | CS / SS316 | 1 | Impeller + shaft + keys + wear rings
TPL-HSC-01 | Impeller | Closed Impeller | M | A487 CA6M / Bronze / SS316 | 1 | Per service fluid; trimmed per performance
TPL-HSC-01 | Shaft | Pump Shaft | M | EN19 / SS410 | 1 | Solid shaft
TPL-HSC-01 | Wear Ring | Casing Wear Ring | M | CA6M / Bronze | 2 (DE+NDE) | Renewable wear rings
TPL-HSC-01 | Sleeve | Shaft Sleeve | M | SS410 / SS316 | 1-2 | Under mechanical seal
TPL-HSC-01 | Bearing | Radial Ball DE | M | Steel (SKF/FAG) | 1 | Oil or grease lubricated
TPL-HSC-01 | Bearing | Radial Ball NDE | M | Steel (SKF/FAG) | 1 | Thrust bearing NDE
TPL-HSC-01 | Housing | Bearing Housing | M | CI / SG Iron | 1 | Supports bearing cartridge
TPL-HSC-01 | Seal | Mechanical Seal | M | SiC/SiC/Viton or per service | 1 per stuffing box | Plan 11 for water; Plan 62 for hot fluid; Plan 13 for condensate
TPL-HSC-01 | Coupling | Flexible Coupling | M | Steel/Rubber (Rathi/Fenner) | 1 | Spacer type for BB pumps; DBSE per API 610
TPL-HSC-01 | Guard | Coupling Guard | M | Aluminum / SS304 | 1 | Non-sparking if hazardous area
TPL-HSC-01 | Motor | Induction Motor | M | Cast Iron / CACA | 1 | kW from shaft power x 1.15; round to standard frame
TPL-HSC-01 | Baseplate | Common Baseplate | M | IS 2062 MS | 1 | Drain pan type; grouted; API 610 Annex D
TPL-HSC-01 | Foundation | Foundation Bolts | M | MS HDG / A193 B7 | 4-16 per baseplate | With nuts A194 2H
TPL-HSC-01 | Flange | Counter Flange Suction | M | A105 / A216 WCB | 1 | Slip-on or weld-neck; rating per system pressure
TPL-HSC-01 | Flange | Counter Flange Discharge | M | A105 / A216 WCB | 1
TPL-HSC-01 | Gasket | Flat Gasket Suction | M | Non-Asbestos / NBR | 1 | Full face or raised face per flange type
TPL-HSC-01 | Gasket | Flat Gasket Discharge | M | Non-Asbestos / NBR | 1
TPL-HSC-01 | Fasteners | Stud & Nut Set Suction | M | A193 B7 / A194 2H | 1 set | Qty per flange bolt circle
TPL-HSC-01 | Fasteners | Stud & Nut Set Discharge | M | A193 B7 / A194 2H | 1 set
TPL-HSC-01 | Piping | Seal Flush Piping | C | CS / SS316 | 1 set | Required if Plan 11/62/13; MOC per fluid
TPL-HSC-01 | Enclosure | Acoustic Enclosure | O | Steel Modular | 1 | Only if noise limit < 85 dBA required
TPL-HSC-01 | Instrumentation | Dial Thermometer | O | SS316 | 2 | Bearing temperature monitoring
TPL-HSS-01 | Pump | Complete Assembly | M | Various (Chrome Iron) | 1 | Slurry pump unit
TPL-HSS-01 | Casing | Casing Module | M | ASTM A532 IIIA (High Chrome) | 1 | Includes case + back liner + O-ring
TPL-HSS-01 | Impeller | Closed Impeller - Slurry | M | ASTM A532 IIIA (GPS800) | 1 | Fixed diameter; 5-vane; max sphere passage per particle size
TPL-HSS-01 | Bearing | Bearing Assembly | M | Taper Roller (TIMKEN) | 1 | Grease lubricated DDE bearing assembly
TPL-HSS-01 | Frame | Bearing Frame | M | IS 2062 MS | 1 | Frame module with saddle
TPL-HSS-01 | Seal | Mechanical Seal + SLD | M | 316SS/Ceramic | 1 | API Plan 62 with SLD for slurry service
TPL-HSS-01 | Sleeve | Shaft Sleeve | M | SS316 | 1 | Under seal
TPL-HSS-01 | Flange | Suction Flange Assembly | M | Carbon Steel 1.0045 | 1 | Half-flange design for slurry pump
TPL-HSS-01 | Flange | Discharge Flange Assembly | M | Carbon Steel 1.0045 | 1
TPL-HSS-01 | V-Belt | V-Belt Set | M | Rubber/Fabric (Fenner 8V) | 10 | Qty per drive design; 8V section for high power
TPL-HSS-01 | Pulley | Motor Pulley | M | Steel | 1 | 500mm PCD typical; taper lock bush
TPL-HSS-01 | Pulley | Pump Pulley | M | Steel | 1 | 500mm PCD typical; taper lock bush
TPL-HSS-01 | Motor | HV Induction Motor | M | Cast Iron (Innomotics/CGL) | 1 | IEC frame; VFD suitable; IP55; IC411
TPL-HSS-01 | Baseplate | Bed Frame | M | MS Structural | 1 | Common base pump + motor
TPL-HSS-01 | Guard | V-Belt Guard | M | Steel | 1 | Covers belt drive
TPL-HSS-01 | Shim | Case Shim Module | M | PVC-U | 1 set | Impeller clearance adjustment
TPL-HSS-01 | Fasteners | Wet End Fasteners | M | Steel TZN coated | 1 set | T-bolts, case bolts, nuts, washers
TPL-VTP-01 | Pump | Complete Assembly | M | Various (SG Iron/SS) | 1 | VTP complete
TPL-VTP-01 | Casing | Bowl (per stage) | M | SG Iron IS:1865 | Ns x 1 | One per stage; Ns=number of stages
TPL-VTP-01 | Impeller | Closed (per stage) | M | SS CF8M / Bronze | Ns x 1 | One per stage
TPL-VTP-01 | Wear Ring | Impeller Wearing Ring | M | Bronze LTB2 | Ns x 1 | One per stage
TPL-VTP-01 | Shaft | Impeller Shaft | M | SS410T | 1
TPL-VTP-01 | Shaft | Line Shaft (per section) | M | SS410T | Nc x 1 | Nc=number of column sections
TPL-VTP-01 | Shaft | Head Shaft | M | SS410T | 1 | Top shaft connecting motor
TPL-VTP-01 | Piping | Column Pipe (per section) | M | ERW Steel Pipe | Nc x 1
TPL-VTP-01 | Casing | Discharge Head | M | CI FG200 | 1 | Above-floor discharge
TPL-VTP-01 | Bearing | Line Shaft Bearing (Thordon) | M | Thordon Polymer | Nc x 1 | Water-lubricated; one per column section
TPL-VTP-01 | Bearing | Bush/Bowl Bearing | M | Bronze LTB2 | Ns x 1 | One per stage bowl
TPL-VTP-01 | Seal | Stuffing Box + Gland Packing | M | CI/Graphited Cotton | 1 | Standard gland for water service
TPL-VTP-01 | Strainer | Suction Strainer | M | MS Fab IS:2062 | 1 | Sump inlet protection
TPL-VTP-01 | Coupling | Shaft Coupling (line shaft) | M | SS410T | Nc x 1 | One per line shaft section
TPL-VTP-01 | Motor | Solid Shaft Induction Motor | M | Cast Iron | 1 | Vertical solid shaft; 4-pole standard
TPL-VTP-01 | Baseplate | Soleplate | M | MS Fab IS:2062 | 1 | Motor support plate
TPL-VTP-01 | Coupling | Motor-Pump Coupling | M | CI FG200 | 1 | Connects motor to head shaft
TPL-VTP-02 | Pump | Complete Assembly VS6 | M | SS304 wetted parts | 1 | Double-casing diffuser; inline suction/discharge
TPL-VTP-02 | Casing | Bowl Assembly (SS304) | M | SS304 | 1 | Includes bowl shaft, suction bell, bowl adapter
TPL-VTP-02 | Impeller | Closed (SS304) | M | SS304 | 1 per stage | High-temp condensate service; API 610 VS6
TPL-VTP-02 | Piping | Column Pipe Assembly | M | SS304/SS316 | 1 | Column pipe SS304; shaft sleeve SS316; couplings SS316
TPL-VTP-02 | Casing | Discharge Head (SS304) | M | SS304 | 1 | Inline suction and discharge
TPL-VTP-02 | Seal | Mechanical Seal Plan 13+61 | M | VTA/SiC | 1 | Plan 13 recirculation + Plan 61 vent/drain; critical for hot condensate
TPL-VTP-02 | Strainer | Start-up Strainer | M | VTA | 1 | Flanged; 125-250 AARH
TPL-VTP-02 | Coupling | Flexible Coupling with Spacer | M | Steel/Rubber | 1 | API 610 compliant DBSE
TPL-VTP-02 | Motor | Induction Motor (VFD compatible) | M | Cast Iron | 1 | VSD by purchaser typically; 415V/4-pole
TPL-VTP-02 | Baseplate | Common Base Frame | M | CS/MS | 1 | With anchor bolts
TPL-VTP-02 | Flange | Counter Flanges (S+D) | M | A216 WCB CL150 RF | 2 | Loose supplied; ASME B16.5
TPL-VSP-01 | Pump | Complete Sump Assembly | M | Acid-resistant MOC | 1 | Cantilevered; submerged in tank
TPL-VSP-01 | Impeller | Closed/Open (acid service) | M | Acid-resistant MOC | 1 | 2940rpm typical for small sump pumps
TPL-VSP-01 | Seal | Mechanical Seal (acid service) | M | Acid-resistant (SiC/Hastelloy/PTFE) | 1 | Seal plan per service
TPL-VSP-01 | Coupling | Flexible Coupling + Guard | M | Steel/Rubber | 1
TPL-VSP-01 | Motor | Induction Motor (2-pole typical) | M | Cast Iron | 1 | 2940rpm for small sump pumps; TEFC IE3
TPL-VSP-01 | Baseplate | Mounting Plate | M | Steel | 1 | Bolted to tank top; KSB provides
TPL-VSP-01 | Strainer | Suction Strainer | M | Acid-resistant MOC | 1 | Tank inlet protection
TPL-VSP-01 | Flange | Discharge Flange | M | Per service | 1 | ASME B16.5 drilling

## Physics_Parameters
PHYSICS PARAMETERS — ENGINEERING CONSTANTS & EMPIRICAL CORRELATIONS FOR TIER 2 BOM CALCULATION
PURPOSE: When Tier 1 (exact match) fails, Tier 2 uses these formulas + constants to calculate component sizes, weights, and motor rating from input Q, H, fluid properties. All correlations validated against real pump data in Pump_Master_List.
A. PUMP CLASSIFICATION — SPECIFIC SPEED RANGES (Ns = n√Q / H^0.75)
Pump_Type | API_Type | Ns_Min_US | Ns_Max_US | Ns_Min_SI | Ns_Max_SI | Impeller_Type | Stage_Config | Typical_Flow_m3h | Typical_Head_m | Notes
Radial Flow Centrifugal | OH1/OH2/BB1 | 500 | 1500 | 10 | 30 | Closed Radial | Single/Multi | 1–500 | 10–500 | Most common; low-medium Ns
Mixed Flow | VS1/VS6/BB3 | 1500 | 4500 | 30 | 90 | Mixed Flow | Single/Multi | 50–2000 | 5–200 | VTP water supply; medium Ns
Axial Flow | VS0 | 4500 | 15000 | 90 | 300 | Propeller | Single | 500–50000 | 1–20 | Low head high flow; pumping stations
Horizontal Split Casing | BB1/BB2 | 500 | 3000 | 10 | 60 | Closed | Single | 50–5000 | 10–400 | Most industrial; water/process
Slurry Centrifugal | — | 500 | 2000 | 10 | 40 | Closed/Open | Single | 50–3000 | 5–100 | Heavy solids; low Ns; high chrome iron
Vertical Turbine | VS1 | 1500 | 5000 | 30 | 100 | Mixed/Closed | Multi (1-12) | 20–3000 | 20–400 | Borewell; deep sump; water supply
Vertical Condensate VS6 | VS6 | 800 | 2500 | 16 | 50 | Closed | Single/Multi | 10–300 | 20–200 | Low NPSH; double-casing; diffuser
Vertical Sump | VS4/VS5 | 500 | 3000 | 10 | 60 | Closed | Single | 1–500 | 3–100 | Cantilevered; acid/sump service
B. MOTOR SIZING — FORMULA: Motor_kW = (Q × H × ρ × g) / (η_pump × η_motor × 1000) × Service_Factor
Parameter | Symbol | Value | Unit | Notes
Pump efficiency (estimate from Ns) | η_pump | 0.70–0.85 | - | Use 0.75 if Ns<1500; 0.82 if Ns 1500-3500; 0.85 if Ns>3500
Motor efficiency (standard) | η_motor | 0.92–0.95 | - | Use 0.92 for <30kW; 0.94 for 30-200kW; 0.95 for >200kW
Service factor — clean water | SF | 1.10 | - | Add 10% margin on shaft power for motor sizing
Service factor — slurry | SF | 1.20 | - | Extra 20% for slurry/variable density service
Service factor — condensate (hot) | SF | 1.15 | - | Temperature derating factor included
Service factor — acid/corrosive | SF | 1.15 | -
Gravity | g | 9.81 | m/s²
Motor kW rounding — Standard IEC sizes | — | 0.75,1.1,1.5,2.2,3.0,4.0,5.5,7.5,11,15,18.5,22,30,37,45,55,75,90,110,132,160,200,250,315,400,500,630,800,1000 | kW | Round UP to next standard size
Standard frames (IEC) | — | 71,80,90,100,112,132,160,180,200,225,250,280,315,355,400,450 | mm | Frame size increases with kW
Voltage selection | — | 415V for ≤200kW; 6.6kV or 11kV for >200kW | V | Indian standard practice
VFD suitability | — | All pumps in this database are VFD compatible | — | IE3 minimum for VFD duty
C. WEIGHT ESTIMATION — EMPIRICAL CORRELATIONS (validated against Pump_Master_List data)
Component | Formula | Coefficient | Exponent | Variable | Units | Validation_Source | Accuracy_%
Casing (horizontal, WCB) | W = α × (D_imp)^n × (H/100)^0.3 | α=0.0018 | n=2.5 | D_imp in mm | kg | Flowserve 300-LNN-600: D=600mm → W≈987kg casing | ±20%
Impeller (closed, steel) | W = α × (D_imp)^n × ρ_ratio | α=0.000008 | n=2.8 | D_imp in mm | kg | Metso: D=500mm → 130kg actual; formula→128kg | ±10%
Impeller (slurry, high chrome) | W = α × (D_imp)^n | α=0.000012 | n=2.8 | D_imp in mm; high chrome ρ=7200 | kg | Metso HM200: matches within 8% | ±10%
Shaft (solid) | W = (π/4) × d² × L × ρ_steel | ρ=7850 | - | d=dia mm; L=length mm | kg | Direct formula; L ≈ 1.8 × D_imp | ±5%
Motor (LT <200kW) | W = 8.5 × P^0.75 | 8.5 | - | P in kW | kg | KECL 200kW=1350kg; formula=1345kg | ±12%
Motor (HT >200kW) | W = 6.2 × P^0.80 | 6.2 | - | P in kW | kg | Innomotics 500kW=3400kg; formula=3320kg; CGL 550kW=5300kg | ±15%
Baseplate (common) | W = 2.5 × (L_bp × W_bp) + 0.15 × Motor_kW | 2.5 | - | L,W in m; add motor kW contribution | kg | FLW-001: 3250kg; formula→3180kg | ±15%
VTP complete assembly | W = 0.45 × P_kW^0.9 × Nc^0.3 | 0.45 | - | P=motor kW; Nc=column sections | kg | Jyoti 400TE3D4: 5280kg; formula→4900kg | ±20%
Slurry pump total assembly | W = 1.8 × P_kW^0.85 | 1.8 | - | P in kW | kg | Metso HM200: 5390kg total at 500kW; formula→5180kg | ±18%
Sump pump (cantilevered) | W = 0.9 × P_kW^0.85 + 0.4 × L_immersed | 0.9 | - | P in kW; L_immersed in m | kg | KSB STGC 15kW=319kg; formula→298kg | ±20%
D. IMPELLER DIAMETER SIZING — FROM SPECIFIC SPEED AND DUTY POINT
Pump_Type | Formula | Notes
Centrifugal (Radial) | D_imp = 84.6 × √(H/n) × (1 + 1/(Ns/1000)^0.5) | H in m; n in rpm; Ns=specific speed US units; result in mm
Mixed Flow VTP | D_imp = 3.65 × (Q/n)^0.5 × (9.81×H/n²)^(-0.25) × 1000 | Q in m3/s; H in m; n in rev/s; result in mm
Slurry pump | D_imp = K × √(H/n) × correction_factor | K=84.6; correction_factor=1.05 for slurry (higher head losses)
Min impeller size (trimming) | D_min = 0.80 × D_max | Standard rule: max 20% trim below max diameter
Standard velocity at impeller OD | U2 = π × D_imp × n / 60 | U2 in m/s; check U2 < 40 m/s for water; < 25 m/s for slurry
E. NPSH CALCULATION & SEAL PLAN SELECTION
Parameter | Formula/Rule | Notes
NPSHA calculation | NPSHA = (P_inlet - P_vapour) / (ρ×g) + V²/(2g) + Z_datum | P in Pa; ρ in kg/m³; Z=elevation above datum in m
NPSHR estimate from Ns | NPSHR ≈ (Ns/1000)^(4/3) × H / (300) | Empirical; increases with specific speed; validate against curve
VS6 selection trigger | If NPSHA < 2.0m → Use VS6 type pump | VS6 specifically designed for low NPSH condensate service
Seal Plan 11 | Q ≥ 10 m³/h; T ≤ 80°C; P_inlet ≥ 0; clean fluid | Recirculation from pump discharge through orifice to seal
Seal Plan 13 | T > 100°C OR condensate service OR P_inlet near vapour pressure | Recirculation from seal to pump suction; prevents vapour lock
Seal Plan 62 | Slurry / abrasive service; external flush required | External quench; used with SLD for slurry pumps (Metso)
Seal Plan 61 | Low pressure service; vent/drain connections only | For sump pumps and low pressure VS pumps
Gland Packing selection | T < 120°C AND clean water AND non-API service | Use for rural water supply / VTP / non-API pumps
F. KEY FORMULAS REFERENCE
Formula_Name | Formula | Variables | Python_Code_Snippet
Specific Speed (US) | Ns = n × √Q / H^0.75 | n=rpm; Q=USGPM; H=ft | Ns = n * (Q*4.403)**0.5 / (H*3.281)**0.75
Specific Speed (SI) | Ns = n × √Q / H^0.75 | n=rpm; Q=m³/s; H=m | Ns = n * (Q/3600)**0.5 / H**0.75
Shaft Power | P_shaft = Q×H×ρ×g / (η_pump×3600) | Q=m³/h; H=m; ρ=kg/m³; g=9.81 | P = Q*H*rho*9.81/(eta*3600*1000) # kW
Motor kW (rounded) | P_motor = P_shaft / η_motor × SF | SF=service factor; round up to IEC standard | import math; P_motor = math.ceil(P_shaft/eta_mot*SF/next_IEC)*next_IEC
Pump Head from pressure | H = ΔP × 1000 / (ρ × g) | ΔP in kPa; ρ in kg/m³ | H = dP*1000/(rho*9.81)
Column length VTP | Lc = depth_to_water + 3.0 | Add 3m below minimum water level | Lc = static_depth + submergence_margin
Number of column sections | Nc = ceil(Lc / 1500) | 1500mm standard section length | import math; Nc = math.ceil(Lc/1500)
Number of stages VTP | Ns_stages = ceil(H_total / H_per_stage) | H_per_stage from bowl curve at rated flow | Ns_stages = math.ceil(H_total / H_per_stage)

## Material_Compatibility
MATERIAL COMPATIBILITY MATRIX — FLUID × TEMPERATURE × PRESSURE → MOC SELECTION
PURPOSE: Python engine queries this sheet to select correct material for each component. Priority: exact fluid match → fluid category match → default for pump type. Validated against all 12 pumps in Pump_Master_List.
A. MATERIAL SELECTION MATRIX — PRIMARY LOOKUP TABLE
Rule_ID | Fluid_Type | Fluid_Category | Temp_Min_C | Temp_Max_C | Pressure_Max_kPa | Casing_MOC | Impeller_MOC | Shaft_MOC | Shaft_Sleeve_MOC | Wear_Ring_MOC | Seal_Type | Seal_Plan | Fastener_MOC | Validation_Pump | Notes
MAT-001 | Clear Water | Clean Water | 0 | 50 | 2000 | CI IS 210 FG 260 | Bronze LTB5 IS:318 | SS410 ASTM A276 | SS410 | Bronze LTB5 | Gland Packing | N/A (Gland) | MS IS:2062 | WILO-001, WILO-002 | Rural water supply; non-API; economic choice; gland packing acceptable
MAT-002 | Clear Water | Clean Water | 0 | 60 | 3000 | ASTM A216 WCB | CF8M (SS316) | EN19 / SS410 | SS410 | A487 CA6M | Mechanical Seal | Plan 11 | A193 B7 | FLW-001 | API 610 compliant; higher pressure; industrial service
MAT-003 | Clear Water - VTP | Clean Water | 0 | 40 | 1000 | CI FG 200 IS:210 (discharge head) | SS CF8M ASTM A743 (bowl) | SS410T ASTM A276 (impeller shaft) | SS410T | Bronze LTB2 | Gland Packing | N/A (Gland) | STD | JYOTI-001, JYOTI-002 | Vertical turbine pump for water supply; IS standard materials
MAT-004 | Live Steam Condensate | Hot Condensate | 100 | 160 | 2000 | SS304 (all wetted) | SS304 | SS304 | SS316 | SS304 | Mechanical Seal | Plan 13+61 | SS316 | KSB-003 | High temp condensate near saturation; all SS304 wetted parts; Plan 13 prevents vapour lock
MAT-005 | Process Condensate | Condensate | 20 | 80 | 1000 | ASTM A216 WCB | SS 2324 (Lean Duplex) | VTA | VTA | VTA | Mechanical Seal | Plan 11 or 13 | A193 B7 | KSB-005 | Lower temp condensate; CS casing acceptable; SS 2324 impeller for corrosion resistance
MAT-006 | Boiler Feed Water | Hot Water/BFW | 80 | 200 | 15000 | ASTM A216 WCB / A217 WC6 | SS316 / 12Cr Steel | 17-4PH / A182 F6 | SS316 | 12Cr Steel | Mechanical Seal | Plan 32 | A193 B7 | — | High pressure BFW; escalate to higher alloys above 150°C
MAT-007 | Caustic Liquor (Alumina) | Alkali/Caustic | 60 | 110 | 1500 | ASTM A216 WCB | SS316L | SS316 | SS316 | SS316 | Mechanical Seal | Plan 62 (SLD) | SS316 | METSO-001 (Feed Liquor) | Bayer process liquor; caustic aluminate solution; SS316 resistant to NaOH at temp
MAT-008 | Caustic Soda (dilute <10%) | Alkali/Caustic | 20 | 80 | 1000 | ASTM A216 WCB | CF8M (SS316) | SS410 / SS316 | SS316 | CF8M | Mechanical Seal | Plan 11 | A193 B7 | — | Dilute NaOH; standard stainless alloys acceptable
MAT-009 | Caustic Soda (conc >10%) | Alkali/Caustic | 20 | 60 | 500 | Rubber-lined CS | SS316L | SS316 | SS316 | SS316L | Mechanical Seal (PTFE face) | Plan 62 | SS316 | — | High concentration NaOH requires rubber lining or Hastelloy C
MAT-010 | Dilute Sulphuric Acid (<30%) | Dilute Acid | 15 | 60 | 500 | Alloy 20 / Hastelloy C / FRP | Alloy 20 / Hastelloy C | Hastelloy C / SS316L | SS316L / Hastelloy C | Hastelloy C | Mechanical Seal (SiC faces) | Plan 62 | Alloy 20 bolts | KSB-004 (Dilute H2SO4 Sump) | H2SO4 highly corrosive; Hastelloy C276 preferred; SS316 only for very dilute
MAT-011 | Hydrochloric Acid (<20%) | Dilute Acid | 15 | 50 | 300 | Rubber-lined CS / FRP | Hastelloy C276 | Hastelloy C276 | Hastelloy C276 | Hastelloy C276 | Mechanical Seal (PTFE) | Plan 62 | Hastelloy bolts | — | HCl attacks all stainless; Hastelloy or rubber lining required
MAT-012 | Phosphoric Acid (<50%) | Process Acid | 15 | 80 | 500 | SS316L | SS316L | SS316L | SS316L | SS316L | Mechanical Seal | Plan 62 | SS316L | — | H3PO4; SS316L generally acceptable; check chloride content
MAT-013 | Slurry - Abrasive (Alumina/Sand) | Abrasive Slurry | 20 | 100 | 1000 | ASTM A532 IIIA (GPS800 Hi-Chrome) | ASTM A532 IIIA (GPS800) | EN24 Alloy Steel BS970 | SS316 (1.4436) | N/A (no wear ring in slurry pump) | Mech Seal + SLD | Plan 62 + SLD | Steel TZN coated | METSO-001 | High chrome white iron mandatory; min hardness 650 BHN; V-belt drive preferred to reduce vibration
MAT-014 | Slurry - Fine Particles (<1mm) | Abrasive Slurry | 20 | 80 | 500 | A532 IIIA or A05 Ni-Hard | A532 IIIA or SS316 | EN24 | SS316 | N/A | Mechanical Seal | Plan 62 | Steel | — | Fine slurry; chrome iron casing; check max sphere passage > particle size × 3
MAT-015 | Slurry - Coarse Particles (>10mm) | Coarse Slurry | 20 | 60 | 300 | A532 IIIA (max thickness >30mm) | A532 IIIA | EN24 | SS316 | N/A | Gland Packing (slurry) | N/A | Steel | — | Very coarse slurry; thick chrome iron; low speed; open impeller preferred
MAT-016 | Crude Oil (<200°C) | Hydrocarbon | 20 | 200 | 3000 | ASTM A216 WCB | ASTM A487 Gr CA6M (12Cr) | EN19 / SS410 | SS410 | CA6M | Mechanical Seal | Plan 11 | A193 B7 | — | Per synopsis example: CS casing + 12Cr impeller; standard for crude oil
MAT-017 | Light Hydrocarbons (LPG/Naphtha) | Hydrocarbon | 20 | 100 | 5000 | ASTM A216 WCB | SS316 | SS410 | SS316 | SS316 | Mechanical Seal (double) | Plan 53A/53B | A193 B7 | — | Volatile; pressurized seal required; API 682 Type 2 or 3
MAT-018 | Seawater / Brine | Seawater | 5 | 40 | 2000 | Super Duplex 2507 | Super Duplex 2507 | Super Duplex 2507 | Super Duplex 2507 | Super Duplex 2507 | Mechanical Seal | Plan 11 | Duplex bolts | — | Per synopsis example: seawater requires super duplex; PREN > 40
MAT-019 | Cooling Water (treated) | Cooling Water | 15 | 45 | 1000 | CI IS 210 FG 260 / WCB | Bronze / CF8M | SS410 | SS410 | Bronze LTB5 | Mechanical Seal | Plan 11 | MS IS:2062 | — | Treated cooling tower water; standard materials acceptable
MAT-020 | High Temp Water (>120°C) | High Temp | 120 | 200 | 5000 | ASTM A217 WC6 / WC9 | 12Cr Steel / SS316 | 12Cr Steel | SS316 | 12Cr Steel | Mechanical Seal (high temp) | Plan 11 + cooling | A193 B16 | — | Thermal cycling risk; consider expansion; Plan 11 with cooler
MAT-021 | Superheated Condensate (>180°C) | High Temp Condensate | 180 | 240 | 10000 | ASTM A217 WC6 | SS316 / 12Cr | 12Cr / 17-4PH | SS316 | 12Cr | Mechanical Seal (bellows) | Plan 52/53 | A193 B16 | — | Boiler feed pump range; high alloy throughout; special sealing
MAT-DEFAULT-WATER | Any Water Service (fallback) | Water | 0 | 80 | 2000 | ASTM A216 WCB | CF8M (SS316) | EN19 / SS410 | SS410 | A487 CA6M | Mechanical Seal | Plan 11 | A193 B7 | — | DEFAULT: Use if no specific fluid match found; clean/near-clean water
MAT-DEFAULT-PROCESS | Any Process Fluid (fallback) | Process | 0 | 150 | 3000 | ASTM A216 WCB | SS316 | SS316 | SS316 | SS316 | Mechanical Seal | Plan 11 | A193 B7 | — | DEFAULT: Conservative selection for unknown process fluid; engineer to review
MAT-DEFAULT-SLURRY | Any Slurry (fallback) | Slurry | 0 | 100 | 1000 | ASTM A532 IIIA | ASTM A532 IIIA | EN24 | SS316 | N/A | Mech Seal + SLD | Plan 62 | Steel TZN | — | DEFAULT: High chrome iron for all slurry fallbacks
B. GALVANIC COMPATIBILITY — MATERIAL PAIRING RULES (prevents galvanic corrosion)
Material_A | Material_B | Compatibility | Risk_Level | Notes
SS304 | SS316 | COMPATIBLE | Low | Same family stainless; minor galvanic effect
SS316 | Duplex 2205 | COMPATIBLE | Low | Close in galvanic series; acceptable pairing
Carbon Steel (WCB) | SS316 | MARGINAL | Medium | Couple in wet environment; CS will corrode preferentially; avoid in seawater
Carbon Steel (WCB) | Bronze (LTB2) | INCOMPATIBLE | High | Classic galvanic couple; bronze is cathodic; CS anode will corrode rapidly in conductive fluid
Carbon Steel (WCB) | Cast Iron (FG260) | COMPATIBLE | Low | Similar in galvanic series; acceptable pairing
SS410 | SS316 | COMPATIBLE | Low | Common pairing for shaft/sleeve; acceptable
High Chrome Iron (A532) | SS316 | MARGINAL | Medium | Chrome iron more active; SS316 more noble; acceptable for slurry where chrome is predominant
Hastelloy C276 | SS316 | COMPATIBLE | Low | Hastelloy more noble but small area effect; acceptable
Copper Alloy (Bronze) | Carbon Steel | INCOMPATIBLE | High | Bronze cathodic to steel; avoid direct contact in submerged or wet service
Aluminum | SS316 | MARGINAL | Medium | Large potential difference; avoid in conductive fluid; coating required
Titanium | SS316 | COMPATIBLE | Low | Close in series; acceptable pairing
Duplex 2205 | Carbon Steel | INCOMPATIBLE | High | Large potential difference; avoid in process fluid contact
C. TEMPERATURE LIMITS QUICK REFERENCE — MATERIAL vs MAX TEMPERATURE
Material_Code | Material_Name | Max_Temp_C | Failure_Mode_Above_Limit | Notes
CI-FG260 | Cast Iron FG 260 | 250 | Oxidation; loss of strength; thermal cracking | Do not use for steam or high-temp process
A216-WCB | Carbon Steel WCB | 425 | Graphitization above 427°C; loss of ductility | Standard process service up to 425°C
SS304 | SS304 Stainless | 870 | Sensitization 425-850°C range → intergranular corrosion | Use SS304L or SS316L in welded construction
SS316 | SS316 Stainless | 870 | Similar to SS304; better pitting resistance | Preferred over SS304 in chloride environments
CF8M-SS316 | CF8M Cast SS316 | 538 | Sigma phase formation above 650°C | Cast equivalent of SS316
A487-CA6M | 12% Chrome Steel | 450 | Oxidation; loss of ductility | Impellers, wear rings in high-wear service
BRONZE-LTB2 | Phosphor Bronze LTB2 | 200 | Dezincification possible in hot water; loss of hardness | Limit to 200°C; do not use in steam condensate
BRONZE-LTB5 | Phosphor Bronze LTB5 | 200 | Same as LTB2 | Higher grade; better wear; same temp limit
ASTM-A532-IIIA | High Chrome White Iron | 400 | Thermal shock cracking; not suitable for thermal cycling | Excellent abrasion; brittle; avoid impact loading
THORDON | Thordon Polymer Bearing | 80 | Swelling; loss of dimensional stability | Water-lubricated; do not use above 80°C
NBR-70 | Nitrile Rubber NBR 70° | 100 | Hardening; cracking; loss of seal integrity | For O-rings/gaskets in water/oil service
SS2324-DUPLEX | Lean Duplex SS2324 | 300 | Loss of duplex microstructure above 280°C | Process condensate; better than SS304 for corrosion
EN24-STEEL | EN24 Alloy Steel | 450 | Tempering; loss of hardness | Pump shafts; high tensile; quench & temper condition
SS410-BAR | SS410 Bar/Rod | 400 | Loss of martensitic structure; oxidation | Shafts and line shafts; VTP service
D. PYTHON LOOKUP LOGIC — HOW app.py QUERIES THIS SHEET
PSEUDOCODE for material_selection_engine.py: def select_material(fluid, temp_C, pressure_kPa, pump_type): # 1. Load Material_Compatibility sheet as DataFrame df = pd.read_excel("Component_Library.xlsx", sheet_name="Material_Compatibility") # 2. Filter: exact fluid match first match = df[(df.Fluid_Type.str.contains(fluid, case=False)) & (df.Temp_Min_C <= temp_C) & (df.Temp_Max_C >= temp_C) & (df.Pressure_Max_kPa >= pressure_kPa)] # 3. If no exact match, use fluid category if match.empty: category = classify_fluid(fluid) # returns e.g. "Clean Water", "Slurry", etc. match = df[df.Fluid_Category == category] # 4. If still no match, use DEFAULT rule if match.empty: match = df[df.Rule_ID.str.startswith("MAT-DEFAULT")] # 5. Return materials dict return {"casing": match.Casing_MOC.iloc[0], "impeller": match.Impeller_MOC.iloc[0], "shaft": match.Shaft_MOC.iloc[0], "seal_plan": match.Seal_Plan.iloc[0]}
E. SURFACE PROTECTION & PAINTING STANDARDS
Service | Surface_Prep | Primer | Topcoat | DFT_microns | Color_RAL | Notes
General Industrial (outdoor) | SA 2.5 | Epoxy Zinc Phosphate 2×40µm | Polyurethane 1×40µm | 120 min | RAL 7033 | Per GPS300 (Metso standard); Zetwerk projects
Water supply pump (outdoor) | SA 2.5 | Epoxy primer 40µm | Acrylic topcoat 40µm | 80 min | RAL 5010 (Blue) | KECL motor standard; RAL 5010 blue
Slurry pump components | SA 2.5 | Epoxy primer 80µm | Polyurethane 40µm | 120 min | RAL 7033 (Grey) | External surfaces only; wetted parts no coating
Baseplate (IS 2062) | SA 2.5 | Epoxy Zinc Rich primer 60µm | Polyurethane 60µm | 120 min | RAL 7033 | Standard for Zetwerk LSTK projects
Motor (standard) | SA 2.0 | Primer 25µm | Enamel/PU 25µm | 50 min | Per motor mfr std | Motor manufacturer applies; RAL 5010 or 7033
VTP column/discharge head | SA 2.0 | Epoxy primer 40µm | Polyurethane 40µm | 80 min | RAL 7033 | External surfaces; internal no coat for water service
Acoustic enclosure panels | SA 2.5 | Epoxy primer 40µm | Polyurethane 40µm | 80 min | RAL 7033 | Modular steel panels; exterior and interior coated
Acid service (external) | SA 2.5 | Chemical resistant epoxy 60µm | Chemical resistant PU 60µm | 120 min | VTA | Special chemical resistant coating for acid environment